## E5
ENG_REF | BUILDING_ZONE | CATEGORY | FLOOR_LEVEL | SEQ_NO | LOCATION | FED_FROM | PROVIDES_POWER_TO | NO_OF_CIRCUITS
16-LVSG-1A | KT | MDB | L16 | 1 | Electrical Plants at Level 15/16 | 15-T-1A | 300 KVAR PFC, 2000A PLIG-IN BUSWAY, 15-ATS-B1
16-LVSG-1B | KT | MDB | L16 | 2 | Electrical Plants at Level 15/16 | 15-T-1B | 15-ATS-B2, 15-ATS-C, 300KVAR PFC
16-LVSG-2A | KT | MDB | L16 | 3 | Electrical Plants at Level 15/16 | 15-T-2A | 300 KVAR PFC, 1600A PLUG-IN BUSWAY, 16-MSMDB-B1, 16-MSMDB-C1
16-LVSG-2B | KT | MDB | L16 | 4 | Electrical Plants at Level 15/16 | 15-T-2B | 15-ATS-B3, 15-MSMDB-B1, 300 KVAR PFC
16-LVSG-3A | KT | MDB | L16 | 5 | Electrical Plants at Level 15/16 | 15-T-3A | 300 KVAR PFC, 1600A PLUG-IN BUSWAY, 16-ATS-B1
16-LVSG-3B | KT | MDB | L16 | 6 | Electrical Plants at Level 15/16 | 15-T-3B | 16-ATS-2, 2000A PLUG-IN BUSWAY, 300 KVAR PFC
B2-LVSG-1A | KT | MDB | B2 | 1 | Tower Base Substation Parking | B2-T-1A | 400KVAR PFC, B2-BSMDB-C1-1, B2-BSMDB-T1-2, B2-BSMDB-T1-1
B2-LVSG-1B | KT | MDB | B2 | 2 | Tower Base Substation Parking | B2-T-1B | B1M-MSMDB-T1-1, 4-BSMDB-T1-1, 400KVAR PFC
B2-LVSG-2 | KT | MDB | B2 | 3 | Tower Base Substation Parking | B2-T-2A & B2-T-2B | 400KVAR PFC, 2-BSMDB-T1-1, B2-ATS-T1-7, B2-ATS-T1-4, B2-BSMDB-T1-3, B2-ATS-T1-8, 400KVAR PFC
B2-LVSG-3 | KT | MDB | B2 | 4 | Tower Base Substation Parking | B2-T-3A & B2-T-3B | 400KVAR PFC, B1M-BSMDB-T1-1, 1-BSMDB-T1-1, B2-ATS-T1-1, B2-ATS-T1-2, B2-ATS-T1-3, B1-MSMDB-T1-1, 400KVAR PFC
B1-LVSG-1 | KT | MDB | B1 | 1 | North Electrical Plant Parking | B1-T-1A & B1-T-1B | 400KVAR PFC, B1-ATS-N-3, B1-ATS-N-4, B1-BSMDB-N-2
B1-LVSG-2 | KT | MDB | B1 | 2 | North Electrical Plant Parking | B1-T-2A & B1-T-2B | 400KVAR PFC, B1-ATS-N-2, B1-ATS-N-7, B1-ATS-N-8, B1-MSMDB-N-2, B1-MSMDB-N-1, 400KVAR PFC
B1-LVSG-3 | KT | MDB | B1 | 3 | North Electrical Plant Parking | B1-T-3A & B1-T-3B | 400KVAR PFC, B1-ATS-N-1, B1-MSMDB-T1-6, B1-MSMDB-A1-1, 400KVAR PFC
B2-LVSG-4 | KT | MDB | B2 | 5 | Tower Base Substation Parking | B2-T-4A & B2-T-4B | 400KVAR PFC, B2-BSMDB-B1-1, B1-ATS-S-2, B1-ATS-B1-1, B3-ATS-S-1, B3-ATS-S-2, 400KVAR PFC
B2-LVSG-5 | KT | MDB | B2 | 6 | Tower Base Substation Parking | B2-T-5A & B2-T-5B | 400KVAR PFC, B2-ATS-S-9, B2-MSMDB-S-4, B1-MSMDB-B1-1, 400KVAR PFC
148-LVSG-1 | KT | MDB | L148 | 1 | Electrical Plants at Level 140/148 | 144-T-1A & 144-T-1B | 300KVAR PFC, 140-ATS-1, 148-MSMDB-1, 162-ATS-5, 148-BSMDB-B1, 300KVAR PFC
162-LVSG-1 | KT | MDB | L162 | 1 | Electrical Plants at Level 162 | 162-T-1A & 162-T-1B | 300KVAR PFC, 162-EMSMDB-1, 162-MSMDB-1, 162-ATS-4, 162-MSMDB-2, 300KVAR PFC
96-LVSG-1 | KT | MDB | L96 | 1 | Electrical Plants at Level 95/96 | 95-T-1A & 95-T-1B | 300KVAR PFC, 1600A PLUG-IN BUSWAY, 95-ATS-1, 89-BSMDB-1, 1600A PLUG-IN BUSWAY, 300KVAR PFC
96-LVSG-2A | KT | MDB | L96 | 2 | Electrical Plants at Level 95/96 | 95-T-2A | 300KVAR PFC, 95-MSMDB-C1, 95-MSMDB-A1, 96-ATS-2, 4000A BUSWAY
96-LVSG-2B | KT | MDB | L96 | 3 | Electrical Plants at Level 95/96 | 95-T-2B | 4000A BUSWAY, 95/96-ATS-6, 88/89-ATS-1, 96-MSMDB-B1, 300KVAR PFC
122-LVSG-1 | KT | MDB | L122 | 1 | Electrical Plants at Level 121/122 | 121-T-1A & 121-T-1B | 300KVAR PFC, 2500A PLUG-IN BUSWAY, 121-BSMDB-1, 300KVAR PFC
122-LVSG-2 | KT | MDB | L122 | 2 | Electrical Plants at Level 121/122 | 121-T-2A & 121-T-2B | 300KVAR PFC, 122-MSMDB-1, 122-ATS-2, 121-ATS-1, 121-MSMDB-C, 121-MSMDB-1, 300KVAR PFC
69-LVSG-1A | KT | MDB | L69 | 1 | Electrical Plants at Level 68/69 | 69-T-1A | 300KVAR PFC, 2500A PLUG-IN BUSWAY, 4000A FEEDER BUSWAY
69-LVSG-1B | KT | MDB | L69 | 2 | Electrical Plants at Level 68/69 | 69-T-1B | 4000A FEEDER BUSWAY, 68-MSMDB-C1, 300KVAR PFC
69-LVSG-2A | KT | MDB | L69 | 3 | Electrical Plants at Level 68/69 | 69-T-2A | 300KVAR PFC, 68-MSMDB-B2, 69-ATS-3, 4000A FEEDER BUSWAY
69-LVSG-2B | KT | MDB | L69 | 4 | Electrical Plants at Level 68/69 | 69-T-2B | 4000A FEEDER BUSWAY, 69-ATS-6, 69-ESMDB-B2, 69-MSMDB-B1, 300KVAR PFC
69-LVSG-3A | KT | MDB | L69 | 5 | Electrical Plants at Level 68/69 | 69-T-2A | 300KVAR PFC, 69-ATS-2, 69-ATS-1, 4000A FEEDER BUSWAY
69-LVSG-3B | KT | MDB | L69 | 6 | Electrical Plants at Level 68/69 | 69-T-2B | 4000A FEEDER BUSWAY, 2500A PLUG-IN BUSWAY, 300KVAR PFC
40-LVSG-1A | KT | MDB | L40 | 1 | Electrical Plants at Level 39/40 | 39-T-1A | 300KVAR PFC, 40-MSMDB-B1, 4000A FEEDER BUSWAY
40-LVSG-1B | KT | MDB | L40 | 2 | Electrical Plants at Level 39/40 | 39-T-1B | 3000A PLUG-IN BUSWAY, 300KVAR PFC
40-LVSG-2A | KT | MDB | L40 | 3 | Electrical Plants at Level 39/40 | 39-T-2A | 300KVAR PFC, 39-MSMDB-A1, 39-MSMDB-A2, 40-ATS-B1, 4000A FEEDER BUSWAY
40-LVSG-2B | KT | MDB | L40 | 4 | Electrical Plants at Level 39/40 | 39-T-2B | 4000A FEEDER BUSWAY, 39-MSMDB-C1, 39-MSMDB-B1, 40-MSMDB-B2, 300KVAR PFC
40-LVSG-3A | KT | MDB | L40 | 5 | Electrical Plants at Level 39/40 | 39-T-3A | 300KVAR PFC, 39-ATS-B1, 39-ATS-C1, 4000A FEEDER BUSWAY
40-LVSG-3B | KT | MDB | L40 | 6 | Electrical Plants at Level 39/40 | 39-T-3B | 4000A FEEDER BUSWAY, 39-ATS-3, 46-ATS-1, 300KVAR PFC
162-EM-LVSG-1 | KT | MDB | L162 | 2 | Electrical Plants at Level 162 | 162-EM-T-1 | 162-ESMDB-3, 162-ATS-1, 162-ATS-4, 164-PFPC-1, 164-SFPC-1, 164-PFPC-2, 164-SFPC-2, 162-EBVSMDB-1
96-EM-LVSG-1 | KT | MDB | L96 | 4 | Electrical Plants at Level 95/96 | 95-EM-T-1 | 88/89-ATS-1, 95-ATS-1, 96-ESMDB-1, 95/96-ATS-6, 95-FPC-1, 95-FPC-2
122-EM-LVSG-1 | KT | MDB | L122 | 3 | Electrical Plants at Level 121/122 | 121-EM-T-1 | 121/122-ATS-3, 122-ESMDB-B1, 121-FPC-2, 121-FPC-1, 122-ESMDB-2, 140-EM-LVSG-1
140-EM-LVSG-1 | KT | MDB | L140 | 1 | Electrical Plants at Level 140/148 | 122-EM-LVSG-1 | 140-ESMDB-1, 140-ATS-1
40-EM-LVSG-1 | KT | MDB | L40 | 7 | Electrical Plants at Level 39/40 | 40-EM-T-1 | 39-ATS-3, 40-ATS-B1, 39-FPC-1, 39-FPC-2, 46-ATS-1, 40-ESMDB-B1-2
69-EM-LVSG-1 | KT | MDB | L69 | 7 | Electrical Plants at Level 68/69 | 69-EM-T-1 | 69-ATS-3, 69-ATS-2, 68-ATS-1, 68-FPC-1, 68-FPC-2, 69-ATS-6, 69-ESMDB-B3
B2-EM-LVSG-1 | KT | MDB | B2 | 7 | Tower Base Substation Parking | B2-EM-T-1 | B2-ATS-T1-1, B2-ATS-T1-2, B2-ATS-T1-3, B2-ATS-T1-4
15-EM-LVSG-1 | KT | MDB | L15 | 1 | Electrical Plants at Level 15/16 | 15-EM-T-1 | 15-ATS-B1, 15-ATS-B2, 15-FPC-1, 15-ATS-B3, 15-ATS-C
16-EM-LVSG-1 | KT | MDB | L16 | 7 | Electrical Plants at Level 15/16 | 16-EM-T-1 | 16-ATS-B1, 16-ATS-2, 15-FPC-2, 39-ATS-C1, 39-ATS-B1
B2-EM-LVSG-2 | KT | MDB | B2 | 8 | Tower Base Substation Parking | B2-EM-T-2 | B2-ESMDB-T1-2, B2-ATS-T1-7, B2-ATS-T1-8, B1-ATS-B1-1
B1-EM-LVSG-1 | KT | MDB | B1 | 1 | North Electrical Generator Plant Parking | B1-EM-T-1 | B1-ATS-N-3, B1-ATS-N-4, B3-PFPC-2, B3-PFPC-3, B3-PFPC-1, B3-SFPC-1
B1-EM-LVSG-2 | KT | MDB | B1 | 2 | North Electrical Generator Plant Parking | B1-EM-T-2 | B1-ATS-N-2, B1-ATS-N-8, B1-ATS-N-7, B1-ESMDB-N-2, B3-SFPC-2, B3-SFPC-3
B2-EM-LVSG-3 | KT | MDB | B2 | 1 | South Electrical Generator Plant Parking | B2-EM-T-3 | B2-ESMDB-S-1, B3-ATS-S-1, B3-ATS-S-2, B2-ATS-S-9, B2-EMSMDB-S-3
4000A FEEDER BUSWAY | KT | BDT | L16 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-1A | 16-LVSG-1B
OFFICE 2000A PLUG-IN BUSWAY | KT | BDT | L16 TO L7 | 1 | MEP Level 16 to Office High Level 7 | 16-LVSG-1A | CB 13-BSMDB-1, CB 12-BSMDB-1, CB 11-BSMDB-1, CB 10-BSMDB-1
4000A FEEDER BUSWAY | KT | BDT | L16 | 2 | Electrical Plants at Level 15/16 | 16-LVSG-2A | 16-LVSG-2B
OFFICE 1600A PLUG-IN BUSWAY | KT | BDT | L16 TO L11 | 2 | MEP Level 16 to Office Low Level 11 | 16-LVSG-2A | CB 9-BSMDB-1, CB 8-BSMDB-1, CB 7-BSMDB-1
4000A FEEDER BUSWAY | KT | BDT | L16 | 3 | MEP Level 16 to Hotel Level 26 | 16-LVSG-3A | 16-LVSG-3B
HOTEL 1600A PLUG-IN BUSWAY | KT | BDT | L16 TO L26 | 3 | MEP Level 16 to Hotel Level 26 | 16-LVSG-3A | CB 18-PDB-1, CB 20-BSMDB-1, CB 21-BSMDB-1, CB 22-BSMDB-1, CB 23-BSMDB-1, CB 24-BSMDB-1, CB 25-BSMDB-1, CB 26-BSMDB-1
SERVICE APARTMENT 2000A PLUG-IN BUSWAY | KT | BDT | L16 TO L38 | 4 | MEP Level 16 to Refuge Area Level 38 | 16-LVSG-3B | CB 27-BSMDB-1, CB 28-BSMDB-1, CB 29-BSMDB-1, CB 30-BSMDB-1, CB 31-BSMDB-1, CB 32-BSMDB-1, CB 33-BSMDB-1, CB 34-BSMDB-1, CB 35-BSMDB-1, CB 36-BSMDB-1
5000A BUSWAY | KT | BDT | B2 | 1 | Tower Base Substation Parking | B2-LVSG-1A | B2-LVSG-1B
RESIDENTIAL GROUP 4 LOW 1600A PLUG-IN BUSWAY | KT | BDT | L96 TO L104 | 1 | MEP Level 96 to Refuge Area Level 104 | 96-LVSG-1 (SIDE-A) | CB 99-BSMDB-1, CB 100-BSMDB-1, CB 101-BSMDB-1, CB 102-BSMDB-1, CB 103-BSMDB-1, CB 104-PDB-1
RESIDENTIAL GROUP 3 1600A PLUG-IN BUSWAY | KT | BDT | L95 TO L86 | 1 | MEP Level 96 to Refuge Area Level 86 | 96-LVSG-1 (SIDE-B) | CB 94-BSMDB-1, CB 93-BSMDB-1, CB 92-BSMDB-1, CB 91-BSMDB-1, CB 90-BSMDB-1, CB 89-BSMDB-1, CB 88-BSMDB-1, CB 87-BSMDB-1, CB 86-BSMDB-1
4000A BUSWAY | KT | BDT | L96 | 2 | Electrical Plants at Level 95/96 | 96-LVSG-2A | 96-LVSG-2B
RESIDENTIAL GROUP 4 HIGH 2500A PLUG-IN BUSWAY | KT | BDT | L122 TO L106 | 1 | MEP Level 122 to Residential Group 4 Level 106 | 122-LVSG-1 (SIDE-A) | CB 120-BSMDB-1, CB 119-BSMDB-1, CB 118-BSMDB-1, CB 117-BSMDB-1, CB 116-BSMDB-1, CB 115-BSMDB-1, CB 114-BSMDB-1, CB 113-BSMDB-1, CB 112-BSMDB-1, CB 111-BSMDB-1, CB 110-BSMDB-1, CB 109-BSMDB-1, CB 107-BSMDB-1, CB 106-BSMDB-1
RESIDENTIAL GROUP 1 HIGH 2500A PLUG-IN BUSWAY | KT | BDT | L68 TO L58 | 1 | MEP Level 68 to Residential Group 1 Level 58 | 69-LVSG-1A | CB 67-BSMDB-1, CB 66-BSMDB-1, CB 65-BSMDB-1, CB 64-BSMDB-1, CB 63-BSMDB-1, CB 62-BSMDB-1, CB 61-BSMDB-1, CB 60-BSMDB-1, CB 59-BSMDB-1, CB 58-BSMDB-1,
4000A FEEDER BUSWAY | KT | BDT | L69 | 1 | MEP Level 69 | 69-LVSG-1A | 69-LVSG-1B
4000A FEEDER BUSWAY | KT | BDT | L69 | 2 | MEP Level 69 | 69-LVSG-2A | 69-LVSG-2B
4000A FEEDER BUSWAY | KT | BDT | L69 | 3 | MEP Level 69 | 69-LVSG-3A | 69-LVSG-3B
RESIDENTIAL GROUP 2 2500A PLUG-IN BUSWAY | KT | BDT | L69 TO L84 | 4 | MEP Level 69 to Sky Lobby Level 84 | 69-LVSG-3B | CB 71-PDB-1, 73-BSMDB-1, 74-BSMDB-1, 75-BSMDB-1, 76-BSMDB-1, 77-BSMDB-1, 78-BSMDB-1, 79-BSMDB-1, 80-BSMDB-1, 81-BSMDB-1, 82-BSMDB-1, 83-BSMDB-1, 84-BSMDB-1
4000A FEEDER BUSWAY | KT | BDT | L40 | 1 | MEP Level 40 | 40-LVSG-1A | 40-LVSG-1B
RESIDENTIAL GROUP 1 LOW 3000A PLUG-IN BUSWAY | KT | BDT | L40 TO L56 | 2 | MEP Level 40 to Refuge Area Level 56 | 40-LVSG-1B | CB 42-BSMDB-1, CB 43-BSMDB-1, CB 44-BSMDB-1, CB 45-BSMDB-1, CB 46-BSMDB-1, CB 47-BSMDB-1, CB 48-BSMDB-1, CB 49-BSMDB-1, CB 50-BSMDB-1, CB 51-BSMDB-1, CB 52-BSMDB-1, CB 53-BSMDB-1, CB 54-BSMDB-1, CB 55-BSMDB-1, 56-PDB-1
4000A FEEDER BUSWAY | KT | BDT | L40 | 3 | MEP Level 40 | 40-LVSG-2A | 40-LVSG-2B
4000A FEEDER BUSWAY | KT | BDT | L40 | 4 | MEP Level 40 | 40-LVSG-3A | 40-LVSG-3B
PFC 300KVAR | KT | PFC | L16 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-1A | 16-LVSG-1A
PFC 300KVAR | KT | PFC | L16 | 2 | Electrical Plants at Level 15/16 | 16-LVSG-1B | 16-LVSG-1B
PFC 300KVAR | KT | PFC | L16 | 3 | Electrical Plants at Level 15/16 | 16-LVSG-2A | 16-LVSG-2A
PFC 300KVAR | KT | PFC | L16 | 4 | Electrical Plants at Level 15/16 | 16-LVSG-2B | 16-LVSG-2B
PFC 300KVAR | KT | PFC | L16 | 5 | Electrical Plants at Level 15/16 | 16-LVSG-3A | 16-LVSG-3A
PFC 300KVAR | KT | PFC | L16 | 6 | Electrical Plants at Level 15/16 | 16-LVSG-3B | 16-LVSG-3B
PFC 400KVAR | KT | PFC | B2 | 1 | Tower Base Substation Parking | B2-LVSG-1A | B2-LVSG-1A
PFC 400KVAR | KT | PFC | B2 | 2 | Tower Base Substation Parking | B2-LVSG-1B | B2-LVSG-1B
PFC 400KVAR | KT | PFC | B2 | 3 | Tower Base Substation Parking | B2-LVSG-2 (SIDE-A) | B2-LVSG-2 (SIDE-A)
PFC 400KVAR | KT | PFC | B2 | 4 | Tower Base Substation Parking | B2-LVSG-2 (SIDE-B) | B2-LVSG-2 (SIDE-B)
PFC 400KVAR | KT | PFC | B2 | 5 | Tower Base Substation Parking | B2-LVSG-3 (SIDE-A) | B2-LVSG-3 (SIDE-A)
PFC 400KVAR | KT | PFC | B2 | 6 | Tower Base Substation Parking | B2-LVSG-3 (SIDE-B) | B2-LVSG-3 (SIDE-B)
PFC 400KVAR | KT | PFC | B1 | 1 | North Electrical Plant Parking | B2-LVSG-1 (SIDE-A) | B2-LVSG-1 (SIDE-A)
PFC 400KVAR | KT | PFC | B1 | 2 | North Electrical Plant Parking | B2-LVSG-1 (SIDE-B) | B2-LVSG-1 (SIDE-B)
PFC 400KVAR | KT | PFC | B1 | 3 | North Electrical Plant Parking | B1-LVSG-2 (SIDE-A) | B1-LVSG-2 (SIDE-A)
PFC 400KVAR | KT | PFC | B1 | 4 | North Electrical Plant Parking | B1-LVSG-2 (SIDE-B) | B1-LVSG-2 (SIDE-B)
PFC 400KVAR | KT | PFC | B1 | 5 | North Electrical Plant Parking | B1-LVSG-3 (SIDE-A) | B1-LVSG-3 (SIDE-A)
PFC 400KVAR | KT | PFC | B1 | 6 | North Electrical Plant Parking | B1-LVSG-3 (SIDE-B) | B1-LVSG-3 (SIDE-B)
PFC 400KVAR | KT | PFC | B2 | 7 | Tower Base Substation Parking | B2-LVSG-4 (SIDE-A) | B2-LVSG-4 (SIDE-A)
PFC 400KVAR | KT | PFC | B2 | 8 | Tower Base Substation Parking | B2-LVSG-4 (SIDE-B) | B2-LVSG-4 (SIDE-B)
PFC 400KVAR | KT | PFC | B2 | 9 | Tower Base Substation Parking | B2-LVSG-5 (SIDE-A) | B2-LVSG-5 (SIDE-A)
PFC 400KVAR | KT | PFC | B2 | 10 | Tower Base Substation Parking | B2-LVSG-5 (SIDE-B) | B2-LVSG-5 (SIDE-B)
PFC 300KVAR | KT | PFC | L148 | 1 | Electrical Plants at Level 140/148 | 148-LVSG-1 (SIDE-A) | 148-LVSG-1 (SIDE-A)
PFC 300KVAR | KT | PFC | L148 | 2 | Electrical Plants at Level 140/148 | 148-LVSG-1 (SIDE-B) | 148-LVSG-1 (SIDE-B)
PFC 300KVAR | KT | PFC | L162 | 1 | Electrical Plants at Level 162 | 162-LVSG-1 (SIDE-A) | 162-LVSG-1 (SIDE-A)
PFC 300KVAR | KT | PFC | L162 | 2 | Electrical Plants at Level 162 | 162-LVSG-1 (SIDE-B) | 162-LVSG-1 (SIDE-B)
PFC 300KVAR | KT | PFC | L96 | 1 | Electrical Plants at Level 95/96 | 96-LVSG-1 (SIDE-A) | 96-LVSG-1 (SIDE-A)
PFC 300KVAR | KT | PFC | L96 | 2 | Electrical Plants at Level 95/96 | 96-LVSG-1 (SIDE-B) | 96-LVSG-1 (SIDE-B)
PFC 300KVAR | KT | PFC | L96 | 3 | Electrical Plants at Level 95/96 | 96-LVSG-2A (SIDE-A) | 96-LVSG-2A (SIDE-A)
PFC 300KVAR | KT | PFC | L96 | 4 | Electrical Plants at Level 95/96 | 96-LVSG-2B (SIDE-B) | 96-LVSG-2B (SIDE-B)
PFC 300KVAR | KT | PFC | L122 | 1 | Electrical Plants at Level 121/122 | 122-LVSG-1 (SIDE-A) | 122-LVSG-1 (SIDE-A)
PFC 300KVAR | KT | PFC | L122 | 2 | Electrical Plants at Level 121/122 | 122-LVSG-1 (SIDE-B) | 122-LVSG-1 (SIDE-B)
PFC 300KVAR | KT | PFC | L122 | 3 | Electrical Plants at Level 121/122 | 122-LVSG-2 (SIDE-A) | 122-LVSG-2 (SIDE-A)
PFC 300KVAR | KT | PFC | L122 | 4 | Electrical Plants at Level 121/122 | 122-LVSG-2 (SIDE-B) | 122-LVSG-2 (SIDE-B)
PFC 300KVAR | KT | PFC | L69 | 1 | Electrical Plants at Level 68/69 | 69-LVSG-1A | 69-LVSG-1A
PFC 300KVAR | KT | PFC | L69 | 2 | Electrical Plants at Level 68/69 | 69-LVSG-1B | 69-LVSG-1B
PFC 300KVAR | KT | PFC | L69 | 3 | Electrical Plants at Level 68/69 | 69-LVSG-2A | 69-LVSG-2A
PFC 300KVAR | KT | PFC | L69 | 4 | Electrical Plants at Level 68/69 | 69-LVSG-2B | 69-LVSG-2B
PFC 300KVAR | KT | PFC | L69 | 5 | Electrical Plants at Level 68/69 | 69-LVSG-3A | 69-LVSG-3A
PFC 300KVAR | KT | PFC | L69 | 6 | Electrical Plants at Level 68/69 | 69-LVSG-3B | 69-LVSG-3B
PFC 300KVAR | KT | PFC | L40 | 1 | Electrical Plants at Level 39/40 | 40-LVSG-1A | 40-LVSG-1A
PFC 300KVAR | KT | PFC | L40 | 2 | Electrical Plants at Level 39/40 | 40-LVSG-1B | 40-LVSG-1B
PFC 300KVAR | KT | PFC | L40 | 3 | Electrical Plants at Level 39/40 | 40-LVSG-2A | 40-LVSG-2A
PFC 300KVAR | KT | PFC | L40 | 4 | Electrical Plants at Level 39/40 | 40-LVSG-2B | 40-LVSG-2B
PFC 300KVAR | KT | PFC | L40 | 5 | Electrical Plants at Level 39/40 | 40-LVSG-3A | 40-LVSG-3A
PFC 300KVAR | KT | PFC | L40 | 6 | Electrical Plants at Level 39/40 | 40-LVSG-3B | 40-LVSG-3B
13-BSMDB-1 | KT | SMDB | L10 | 1 | Office Level 10 | 630A CB | 13-PDB-1, 13-BSMDB-2, 13-BSMDB-3
13-BSMDB-2 | KT | SMDB | L10 | 2 | Office Level 10 | 13-BSMDB-1 | TBC
13-BSMDB-3 | KT | SMDB | L10 | 3 | Office Level 10 | 13-BSMDB-1 | TBC
12-BSMDB-1 | KT | SMDB | L9 | 1 | Office Level 9 | 630A CB | 12-PDB-1, 12-BSMDB-2, 12-BSMDB-3
12-BSMDB-2 | KT | SMDB | L9 | 2 | Office Level 9 | 12-BSMDB-1 | TBC
12-BSMDB-3 | KT | SMDB | L9 | 3 | Office Level 9 | 12-BSMDB-1 | TBC
11-BSMDB-1 | KT | SMDB | L8 | 1 | Office Level 8 | 630A CB | 11-PDB-1, 11-BSMDB-2, 11-BSMDB-3
11-BSMDB-2 | KT | SMDB | L8 | 2 | Office Level 8 | 11-BSMDB-1 | TBC
11-BSMDB-3 | KT | SMDB | L8 | 3 | Office Level 8 | 11-BSMDB-1 | TBC
10-BSMDB-1 | KT | SMDB | L7 | 1 | Office Level 7 | 630A CB | 10-PDB-1, 10-BSMDB-2, 10-BSMDB-3
10-BSMDB-2 | KT | SMDB | L7 | 2 | Office Level 7 | 10-BSMDB-1 | METER
10-BSMDB-3 | KT | SMDB | L7 | 3 | Office Level 7 | 10-BSMDB-1 | METER
9-BSMDB-1 | KT | SMDB | L13 | 1 | Office Level 13 | 630A CB | 9-PDB-1, 9-BSMDB-2, 9-BSMDB-3
9-BSMDB-2 | KT | SMDB | L13 | 2 | Office Level 13 | 9-BSMDB-1 | TBC
9-BSMDB-3 | KT | SMDB | L13 | 3 | Office Level 13 | 9-BSMDB-1 | TBC
8-BSMDB-1 | KT | SMDB | L12 | 1 | Office Level 12 | 630A CB | 8-PDB-1, 8-BSMDB-2, 8-BSMDB-3
8-BSMDB-2 | KT | SMDB | L12 | 2 | Office Level 12 | 8-BSMDB-1 | TBC
8-BSMDB-3 | KT | SMDB | L12 | 3 | Office Level 12 | 8-BSMDB-1 | TBC
7-BSMDB-1 | KT | SMDB | L11 | 1 | Office Level 11 | 630A CB | 7-PDB-1, 7-BSMDB-2, 7-BSMDB-3
7-BSMDB-2 | KT | SMDB | L11 | 2 | Office Level 11 | 7-BSMDB-1 | METER
7-BSMDB-3 | KT | SMDB | L11 | 3 | Office Level 11 | 7-BSMDB-1 | METER
16-MSMDB-B1 | KT | SMDB | L16 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-2A | 16-PDB-1, 16-MDB-A1, 16-MDB-A2, 16-MDB-B1, 16-MDB-B2, VFD MAU-16-2, VFD RF-16-2
16-MSMDB-C1 | KT | SMDB | L16 | 2 | Electrical Plants at Level 15/16 | 16-LVSG-2A | 16-MDB-C1, VFD CHWP-16-1, VFD CHWP-16-2, VFD CHWP-16-3, 3 NOS. WH-2
15-MSMDB-B1 | KT | SMDB | L15 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-2B | 15-MDB-A1, 15-MDB-A2, 15-MDB-B1, 15-MDB-C1, 15-PDB-1, VFD CHWP-15-1, VFD CHWP-15-2
20-BSMDB-1 | KT | SMDB | L20 | 1 | Hotel Level 20 | 300A CB | 20-PDB-1, 20-BSMDB-2, 20-BSMDB-3
20-BSMDB-2 | KT | SMDB | L20 | 2 | Hotel Level 20 | 20-BSMDB-1 | TBC
20-BSMDB-3 | KT | SMDB | L20 | 3 | Hotel Level 20 | 20-BSMDB-1 | TBC
21-BSMDB-1 | KT | SMDB | L21 | 1 | Hotel Level 21 | 300A CB | 21-PDB-1, 21-BSMDB-2, 21-BSMDB-3
21-BSMDB-2 | KT | SMDB | L21 | 2 | Hotel Level 21 | 21-BSMDB-1 | TBC
21-BSMDB-3 | KT | SMDB | L21 | 3 | Hotel Level 21 | 21-BSMDB-1 | TBC
22-BSMDB-1 | KT | SMDB | L22 | 1 | Hotel Level 22 | 300A CB | 22-PDB-1, 22-BSMDB-2, 22-BSMDB-3
22-BSMDB-2 | KT | SMDB | L22 | 2 | Hotel Level 22 | 22-BSMDB-1 | TBC
22-BSMDB-3 | KT | SMDB | L22 | 3 | Hotel Level 22 | 22-BSMDB-1 | TBC
23-BSMDB-1 | KT | SMDB | L23 | 1 | Hotel Level 23 | 300A CB | 23-PDB-1, 23-BSMDB-2, 23-BSMDB-3
23-BSMDB-2 | KT | SMDB | L23 | 2 | Hotel Level 23 | 23-BSMDB-1 | TBC
23-BSMDB-3 | KT | SMDB | L23 | 3 | Hotel Level 23 | 23-BSMDB-1 | TBC
24-BSMDB-1 | KT | SMDB | L24 | 1 | Hotel Level 24 | 300A CB | 24-PDB-1, 24-BSMDB-2, 24-BSMDB-3
24-BSMDB-2 | KT | SMDB | L24 | 2 | Hotel Level 24 | 24-BSMDB-1 | TBC
24-BSMDB-3 | KT | SMDB | L24 | 3 | Hotel Level 24 | 24-BSMDB-1 | TBC
25-BSMDB-1 | KT | SMDB | L25 | 1 | Hotel Level 25 | 300A CB | 25-PDB-1, 25-BSMDB-2, 25-BSMDB-3
25-BSMDB-2 | KT | SMDB | L25 | 2 | Hotel Level 25 | 25-BSMDB-1 | TBC
25-BSMDB-3 | KT | SMDB | L25 | 3 | Hotel Level 25 | 25-BSMDB-1 | TBC
26-BSMDB-1 | KT | SMDB | L26 | 1 | Hotel Level 26 | 300A CB | 26-PDB-1, 26-BSMDB-2, 26-BSMDB-3
26-BSMDB-2 | KT | SMDB | L26 | 2 | Hotel Level 26 | 26-BSMDB-1 | TBC
26-BSMDB-3 | KT | SMDB | L26 | 3 | Hotel Level 26 | 26-BSMDB-1 | TBC
27-BSMDB-1 | KT | SMDB | L27 | 1 | Service Apartments Level 27 | 150A CB | TBC
28-BSMDB-1 | KT | SMDB | L28 | 1 | Service Apartments Level 28 | 150A CB | 28-PDB-1, 28-BSMDB-2, 28-BSMDB-3
28-BSMDB-2 | KT | SMDB | L28 | 2 | Service Apartments Level 28 | 28-BSMDB-1 | TBC
28-BSMDB-3 | KT | SMDB | L28 | 3 | Service Apartments Level 28 | 28-BSMDB-1 | TBC
29-BSMDB-1 | KT | SMDB | L29 | 1 | Service Apartments Level 29 | 150A CB | 29-PDB-1, 29-BSMDB-2, 29-BSMDB-3
29-BSMDB-2 | KT | SMDB | L29 | 2 | Service Apartments Level 29 | 29-BSMDB-1 | TBC
29-BSMDB-3 | KT | SMDB | L29 | 3 | Service Apartments Level 29 | 29-BSMDB-1 | TBC
30-BSMDB-1 | KT | SMDB | L30 | 1 | Service Apartments Level 30 | 150A CB | 30-PDB-1, 30-BSMDB-2, 30-BSMDB-3
30-BSMDB-2 | KT | SMDB | L30 | 2 | Service Apartments Level 30 | 30-BSMDB-1 | TBC
30-BSMDB-3 | KT | SMDB | L30 | 3 | Service Apartments Level 30 | 30-BSMDB-1 | TBC
31-BSMDB-1 | KT | SMDB | L31 | 1 | Service Apartments Level 31 | 150A CB | 31-PDB-1, 31-BSMDB-2, 31-BSMDB-3
31-BSMDB-2 | KT | SMDB | L31 | 2 | Service Apartments Level 31 | 31-BSMDB-1 | TBC
31-BSMDB-3 | KT | SMDB | L31 | 3 | Service Apartments Level 31 | 31-BSMDB-1 | TBC
32-BSMDB-1 | KT | SMDB | L32 | 1 | Service Apartments Level 32 | 150A CB | 32-PDB-1, 32-BSMDB-2, 32-BSMDB-3
32-BSMDB-2 | KT | SMDB | L32 | 2 | Service Apartments Level 32 | 32-BSMDB-1 | TBC
32-BSMDB-3 | KT | SMDB | L32 | 3 | Service Apartments Level 32 | 32-BSMDB-1 | TBC
33-BSMDB-1 | KT | SMDB | L33 | 1 | Service Apartments Level 33 | 150A CB | 33-PDB-1, 33-BSMDB-2, 33-BSMDB-3
33-BSMDB-2 | KT | SMDB | L33 | 2 | Service Apartments Level 33 | 33-BSMDB-1 | TBC
33-BSMDB-3 | KT | SMDB | L33 | 3 | Service Apartments Level 33 | 33-BSMDB-1 | TBC
34-BSMDB-1 | KT | SMDB | L34 | 1 | Service Apartments Level 34 | 150A CB | 34-PDB-1, 34-BSMDB-2, 34-BSMDB-3
34-BSMDB-2 | KT | SMDB | L34 | 2 | Service Apartments Level 34 | 34-BSMDB-1 | TBC
34-BSMDB-3 | KT | SMDB | L34 | 3 | Service Apartments Level 34 | 34-BSMDB-1 | TBC
35-BSMDB-1 | KT | SMDB | L35 | 1 | Service Apartments Level 35 | 150A CB | 35-PDB-1, 35-BSMDB-2, 35-BSMDB-3
35-BSMDB-2 | KT | SMDB | L35 | 2 | Service Apartments Level 35 | 35-BSMDB-1 | TBC
35-BSMDB-3 | KT | SMDB | L35 | 3 | Service Apartments Level 35 | 35-BSMDB-1 | TBC
36-BSMDB-1 | KT | SMDB | L36 | 1 | Service Apartments Level 36 | 150A CB | 36-PDB-1, 36-BSMDB-2, 36-BSMDB-3
36-BSMDB-2 | KT | SMDB | L36 | 2 | Service Apartments Level 36 | 36-BSMDB-1 | TBC
36-BSMDB-3 | KT | SMDB | L36 | 3 | Service Apartments Level 36 | 36-BSMDB-1 | TBC
37-BSMDB-1 | KT | SMDB | L37 | 1 | Service Apartments Level 37 | 150A CB | 37-PDB-1, 37-BSMDB-2, 37-BSMDB-3
37-BSMDB-2 | KT | SMDB | L37 | 2 | Service Apartments Level 37 | 37-BSMDB-1 | TBC
37-BSMDB-3 | KT | SMDB | L37 | 3 | Service Apartments Level 37 | 37-BSMDB-1 | TBC
38-BSMDB-1 | KT | SMDB | L38 | 1 | Service Apartments Level 38 | 150A CB | 38-PDB-1, 38-BSMDB-2, 38-BSMDB-3
38-BSMDB-2 | KT | SMDB | L38 | 2 | Service Apartments Level 38 | 38-BSMDB-1 | TBC
38-BSMDB-3 | KT | SMDB | L38 | 3 | Service Apartments Level 38 | 38-BSMDB-1 | TBC
B2-BSMDB-C1-1 | KT | SMDB | B2 | 1 | Parking/MEP Level B2 | B2-LVSG-1A | B2-BSMDB-C2-1
B2-BSMDB-C2-1 | KT | SMDB | B2 | 2 | Parking/MEP Level B2 | B2-BSMDB-C1-1 | B3-SLDB-C2-1, B3-SPDB-C2-1, B3-LDB-C2, B3-PDB-C2-1
B2-BSMDB-T1-2 | KT | SMDB | B2 | 3 | Parking/MEP Level B2 | B2-LVSG-1A | B1M-LDB-T1, B1-LDB-T1, B2-LDB-T2, B2-PDB-T2, B2-LDB-T1-1, B1-PDB-T1-1, B1-PDB-T1-2, B2-PDB-T1-1, B2-PDB-T1-2, B2-PDB-T1-3, B3-PDB-T1-1, B3-PDB-T3-1
B2-BSMDB-T1-1 | KT | SMDB | B2 | 4 | Parking/MEP Level B2 | B2-LVSG-1A | KITCHEN LOADS, BALLROOM LOADS
B1M-MSMDB-T1-1 | KT | SMDB | B1M | 1 | B1 Mezzanine | B2-LVSG-1B | B1M-FPDB-T1-1, B1M-FPDB-T1-2, B1M-FPDB-T1-3, B1M-MDB-T1-1, B1M-MDB-T1-2, B1M-MDB-T1-3, WH-1
1-MSMDB-T1-1 | KT | SMDB | L1 | 1 | Lobby/Amenities Level 1 | B1M-MSMDB-T1-1 | 4NOS. OF WH-1
4-BSMDB-T1-1 | KT | SMDB | L4 | 1 | Spa Level 4 | B2-LVSG-1B | METERS, 4-PDB-T1-1, 4-LDB-1, 4-MDB-T1-1, 4-MDB-T1-1
2-BSMDB-T1-1 | KT | SMDB | L2 | 1 | Lobby/Amenities Level 2 | B2-LVSG-2 (SIDE-A) | METER, 2-PDB-T1-1, 2-LDB-1, 2-LDB-T1-2, 2-MDB-T1-1, 2-MDB-T1-2
B2-BSMDB-T1-3 | KT | SMDB | B2 | 5 | Parking/MEP Level B2 | B2-LVSG-2 (SIDE-B) | B2-ATS-T1-5, B2-ATS-T1-6
B1M-BSMDB-T1-1 | KT | SMDB | B1M | 2 | B1 Mezzanine | B2-LVSG-3 (SIDE-A) | METER, B1M-PDB-T1-1, B1M-LDB-T1
1-BSMDB-T1-1 | KT | SMDB | L1 | 2 | Lobby/Amenities Level 1 | B2-LVSG-3 (SIDE-A) | METER, 1-PDB-T1-1, 1-LDB-T1-1, 1-LDB-T1-2, 1-MDB-T1-1, 1-MDB-T1-2, 4NOS. ES
B1-MSMDB-T1-1 | KT | SMDB | B1 | 1 | Parking Level B1 | B2-LVSG-3 (SIDE-B) | B1-MDB-T1-1, B1-MDB-C1-1, B1-MDB-C2-1, B2-MDB-C1-1, B2-MDB-T1-1, B2-MDB-T1-2, B3-MDB-C1-1, B3-MDB-C2-1
B1-BSMDB-N-2 | KT | SMDB | B1 | 2 | Parking Level B1 | B1-LVSG-1 (SIDE-B) | B1-BSMDB-N-1, B1-BSMDB-A2-1, B1-BSMDB-N-3, B1-BSMDB-A1-1
B1-BSMDB-N-1 | KT | SMDB | B1 | 3 | Parking Level B1 | B1-BSMDB-N-2 | B3-PDB-N-1, B3-LDB-N1, B1-LDB-N1, B1-PDB-N1-1, B1-PDB-N1-2
B1-BSMDB-A2-1 | KT | SMDB | B1 | 4 | Parking Level B1 | B1-BSMDB-N-2 | B1M-PDB-A2-1, B1-PDB-A2-1, B1-LDB-A2, B2-PDB-A2-1, B3-PDB-A2-1, B3-LDB-A2
B1-BSMDB-N-3 | KT | SMDB | B1 | 5 | Parking Level B1 | B1-BSMDB-N-2 | B1M-SPDB-A2-1, B1-SPDB-N-1, B1-SLDB-N-1, B1M-SLDB-A2-1
B1-BSMDB-A1-1 | KT | SMDB | B1 | 6 | Parking Level B1 | B1-BSMDB-N-2 | B3-PDB-A1-1, B3-LDB-A1-1, METER
B1-MSMDB-N-2 | KT | SMDB | B1 | 7 | Parking Level B1 | B1-LVSG-2 (SIDE-B) | VFD CHWP (B1-1, B1-2, B1-3, B1-4, B1-7)
B1-MSMDB-N-1 | KT | SMDB | B1 | 8 | Parking Level B1 | B1-LVSG-2 (SIDE-B) | VFD CHWP (B1-8, B1-9, B1-10, B1-19, B1-20, B1-21)
B1-BSMDB-A1-2 | KT | SMDB | B1 | 9 | Parking Level B1 | B1-LVSG-2 (SIDE-B) | TBC
B1-MSMDB-T1-6 | KT | SMDB | B1 | 10 | Parking Level B1 | B1-LVSG-3 (SIDE-A) | B1-ATS-N-5, B1-ATS-N-6
B1-MSMDB-A1-1 | KT | SMDB | B2 | 6 | Parking/MEP Level B2 | B1-LVSG-3 (SIDE-B) | B1-MDB-A1-1, B1-MDB-A1-2, B2-MDB-A2-1, B3-MDB-A1-1, B3-MDB-A2-1
B2-BSMDB-B1-1 | KT | SMDB | B2 | 7 | Parking/MEP Level B2 | B2-LVSG-4 (SIDE-A) | B1-PDB-B1-1, B1-LDB-B1, B2-PDB-B1-1, B2-PDB-B1-2, B2-LDB-T2, B2-PDB-T2, B3-PDB-B1-1, B3-LDB-B1, B1M-PDB-B1-1
B2-MSMDB-B1-1 | KT | SMDB | B2 | 8 | Parking/MEP Level B2 | B2-LVSG-4 (SIDE-B) | B1-MDB-B1-1, B1-MDB-B2-1, B2-MDB-B1-1, B2-MDB-B2-1, B3-MDB-B1-1, B3-MDB-B2-1, CB WH-1
B2-MSMDB-S-4 | KT | SMDB | B2 | 9 | Parking/MEP Level B2 | B2-LVSG-5 (SIDE-B) | B2-ATS-S-8, B2-ATS-S-6, B2-ATS-S-7, B2-BSMDB-S-1
B2-BSMDB-S-1 | KT | SMDB | B2 | 10 | Parking/MEP Level B2 | B2-MSMDB-S-4 | B1M-SPDB-B1-1, B1M-SLDB-B1-1, B1-LDB-B2, B1-PDB-B2-1, B2-PDB-B2-1, B2-SPDB-S-1, B2-SLDB-S-1, B3-PDB-B2-1, B3-LDB-B2, B2-LDB-S, B3-PDB-S-1
B1-MSMDB-B1-1 | KT | SMDB | B1 | 11 | Parking Level B1 | B2-LVSG-5 (SIDE-B) | VFD TTEF (B1-1, B1-2, B1-3, B1-4, B1-5), VFD LDEF (B1-3, B1-4) & VFD LDSF-B1-2
148-MSMDB-1 | KT | SMDB | L148 | 1 | Electrical Plants at Level 140/148 | 148-LVSG-1 (SIDE-A) | VFD CHWP-146-1 & 2, 146-MDB-1, 146-MDB-2, 144-MDB-1, 134-MDB-1
148-BSMDB-B1 | KT | SMDB | L148 | 2 | Electrical Plants at Level 140/148 | 148-LVSG-1 (SIDE-B) | 140-ATS-2, 140-ATS-3, 132-PDB-1, 140-PDB-1, 146-PDB-1
162-EMSMDB-1 | KT | SMDB | L162 | 1 | MEP Level 162 | 162-LVSG-1 (SIDE-A) | 162-ATS-1, 162-ATS-2, 162-ATS-3
162-MSMDB-1 | KT | SMDB | L162 | 2 | MEP Level 162 | 162-LVSG-1 (SIDE-A) | 162-BSMDB-1, 162-ATS-6
162-BSMDB-1 | KT | SMDB | L162 | 3 | MEP Level 162 | 162-MSMDB-1 | 148-PDB-1, 152-PDB-1, 157-PDB-1, 162-PDB-1, 168-PDB-1, 184-PDB-1, 203-PDB-1, 222-PDB-1
162-MSMDB-2 | KT | SMDB | L162 | 4 | MEP Level 162 | 162-LVSG-1 (SIDE-B) | 162-MSMDB-3, 155-MSMDB-1
162-MSMDB-3 | KT | SMDB | L162 | 5 | MEP Level 162 | 162-MSMDB-2 | 161-MDB-1, 162-MDB-1, 164-MDB-1, 165-MDB-1, 169-MDB-1, VFD AHU (161-1, 161-2, 161-3), VFD CHWP (161-1, 161-2)
155-MSMDB-1 | KT | SMDB | L155 | 1 | BMU/MEP Level 155 | 162-MSMDB-2 | VFD CHWP (155-2, 155-3, 155-4), 155-MDB-1
99-BSMDB-1 | KT | SMDB | L99 | 1 | Residential Group 4 Level 99 | 200A CB | METER, 99-PDB-1
100-BSMDB-1 | KT | SMDB | L100 | 1 | Residential Group 4 Level 100 | 200A CB | METER, 100-PDB-1
101-BSMDB-1 | KT | SMDB | L101 | 1 | Residential Group 4 Level 101 | 200A CB | METER, 101-PDB-1
102-BSMDB-1 | KT | SMDB | L102 | 1 | Residential Group 4 Level 102 | 200A CB | METER, 102-PDB-1
103-BSMDB-1 | KT | SMDB | L103 | 1 | Residential Group 4 Level 103 | 200A CB | METER, 103-PDB-1
89-BSMDB-1 | KT | SMDB | L89 | 1 | Residential Group 3 Level 89 | 96-LVSG-1 (SIDE-B) | 96-ATS-5, 96-ATS-4
94-BSMDB-1 | KT | SMDB | L94 | 1 | Residential Group 3 Level 94 | 300A CB | 94-BSMDB-2, METER, 94-PDB-1
94-BSMDB-2 | KT | SMDB | L94 | 2 | Residential Group 3 Level 94 | 94-BSMDB-1 | METER
93-BSMDB-1 | KT | SMDB | L93 | 1 | Residential Group 3 Level 93 | 300A CB | 93-BSMDB-2, METER, 93-PDB-1
93-BSMDB-2 | KT | SMDB | L93 | 2 | Residential Group 3 Level 93 | 93-BSMDB-1 | METER
92-BSMDB-1 | KT | SMDB | L92 | 1 | Residential Group 3 Level 92 | 300A CB | 92-BSMDB-2, METER, 92-PDB-1
92-BSMDB-2 | KT | SMDB | L92 | 2 | Residential Group 3 Level 92 | 92-BSMDB-1 | METER
91-BSMDB-1 | KT | SMDB | L91 | 1 | Residential Group 3 Level 91 | 300A CB | 91-BSMDB-2, METER, 91-PDB-1
91-BSMDB-2 | KT | SMDB | L91 | 2 | Residential Group 3 Level 91 | 91-BSMDB-1 | METER
90-BSMDB-1 | KT | SMDB | L90 | 1 | Residential Group 3 Level 90 | 300A CB | 90-BSMDB-2, METER, 90-PDB-1
90-BSMDB-2 | KT | SMDB | L90 | 2 | Residential Group 3 Level 90 | 90-BSMDB-1 | METER
89-BSMDB-1 | KT | SMDB | L89 | 2 | Residential Group 3 Level 89 | 300A CB | 89-BSMDB-2, METER, 89-PDB-1
89-BSMDB-2 | KT | SMDB | L89 | 3 | Residential Group 3 Level 89 | 89-BSMDB-1 | METER
88-BSMDB-1 | KT | SMDB | L88 | 1 | Residential Group 3 Level 88 | 300A CB | 88-BSMDB-2, METER, 88-PDB-1
88-BSMDB-2 | KT | SMDB | L88 | 2 | Residential Group 3 Level 88 | 88-BSMDB-1 | METER
87-BSMDB-1 | KT | SMDB | L87 | 1 | Residential Group 3 Level 87 | 300A CB | 87-BSMDB-2, METER, 87-PDB-1
87-BSMDB-2 | KT | SMDB | L87 | 2 | Residential Group 3 Level 87 | 87-BSMDB-1 | METER
95-MSMDB-C1 | KT | SMDB | L95 | 1 | MEP Level 95 | 96-LVSG-2A | 3NOS. WH-5, VFD CHWP (95-9, 95-10, 95-11), 95-MDB-C1, 95-MDB-C2
95-MSMDB-A1 | KT | SMDB | L95 | 2 | MEP Level 95 | 96-LVSG-2A | VFD CHWP (95-1, 95-2, 95-3, 95-4, 95-5), 95-MDB-A1, 95-MDB-A2, 95-PDB-1
96-MSMDB-B1 | KT | SMDB | L96 | 1 | MEP Level 96 | 96-LVSG-2B | VFD CHWP (96-1, 96-2, 96-3), 96-MDB-A1, 96-MDB-B1, 96-MDB-C1, 96-MDB-C2
120-BSMDB-1 | KT | SMDB | L120 | 1 | Residential Group 4 Level 120 | 200A CB | METER, 120-PDB-1
119-BSMDB-1 | KT | SMDB | L119 | 1 | Residential Group 4 Level 119 | 200A CB | METER, 119-PDB-1
118-BSMDB-1 | KT | SMDB | L118 | 1 | Residential Group 4 Level 118 | 200A CB | METER, 118-PDB-1
117-BSMDB-1 | KT | SMDB | L117 | 1 | Residential Group 4 Level 117 | 200A CB | METER, 117-PDB-1
116-BSMDB-1 | KT | SMDB | L116 | 1 | Residential Group 4 Level 116 | 200A CB | METER, 116-PDB-1
115-BSMDB-1 | KT | SMDB | L115 | 1 | Residential Group 4 Level 115 | 200A CB | METER, 115-PDB-1
114-BSMDB-1 | KT | SMDB | L114 | 1 | Residential Group 4 Level 114 | 200A CB | METER, 114-PDB-1
113-BSMDB-1 | KT | SMDB | L113 | 1 | Residential Group 4 Level 113 | 200A CB | METER, 113-PDB-1
112-BSMDB-1 | KT | SMDB | L112 | 1 | Residential Group 4 Level 112 | 200A CB | METER, 112-PDB-1
111-BSMDB-1 | KT | SMDB | L111 | 1 | Residential Group 4 Level 111 | 200A CB | METER, 111-PDB-1
110-BSMDB-1 | KT | SMDB | L110 | 1 | Residential Group 4 Level 110 | 200A CB | METER, 110-PDB-1
109-BSMDB-1 | KT | SMDB | L109 | 1 | Residential Group 4 Level 109 | 200A CB | METER, 109-PDB-1
108-BSMDB-1 | KT | SMDB | L108 | 1 | Residential Group 4 Level 108 | 200A CB | METER, 108-PDB-1
107-BSMDB-1 | KT | SMDB | L107 | 1 | Residential Group 4 Level 107 | 200A CB | METER, 107-PDB-1
106-BSMDB-1 | KT | SMDB | L106 | 1 | Residential Group 4 Level 106 | 200A CB | METER, 106-PDB-1
121-BSMDB-1 | KT | SMDB | L121 | 1 | MEP Level 121 | 122-LVSG-1 (SIDE-B) | 121/122-ATS-3, 122-ATS-5, 122-ATS-4
122-MSMDB-1 | KT | SMDB | L122 | 1 | MEP Level 122 | 122-LVSG-2 (SIDE-A) | 124-PDB-1, 122-MDB-1, 122-MDB-2
121-MSMDB-C | KT | SMDB | L121 | 2 | MEP Level 121 | 122-LVSG-2 (SIDE-B) | 2NOS, CB WH-6, 121-MDB-C1
121-MSMDB-1 | KT | SMDB | L121 | 3 | MEP Level 121 | 122-LVSG-2 (SIDE-B) | CB WH-6, VFD CHWP (121-1, 121-2, 121-3, 121-5), 121-MDB-A1, 121-MDB-B1
67-BSMDB-1 | KT | SMDB | L67 | 1 | Residential Group 4 Level 67 | 400A CB | METER, 67-PDB-1, 67-BSMDB-2, 67-BSMDB-3
67-BSMDB-2 | KT | SMDB | L67 | 2 | Residential Group 4 Level 67 | 67-BSMDB-1 | METER
67-BSMDB-3 | KT | SMDB | L67 | 3 | Residential Group 4 Level 67 | 67-BSMDB-1 | METER
66-BSMDB-1 | KT | SMDB | L66 | 1 | Residential Group 4 Level 66 | 400A CB | METER, 66-PDB-1, 66-BSMDB-2, 66-BSMDB-3
66-BSMDB-2 | KT | SMDB | L66 | 2 | Residential Group 4 Level 66 | 66-BSMDB-1 | METER
66-BSMDB-3 | KT | SMDB | L66 | 3 | Residential Group 4 Level 66 | 66-BSMDB-1 | METER
65-BSMDB-1 | KT | SMDB | L65 | 1 | Residential Group 4 Level 65 | 400A CB | METER, 65-PDB-1, 65-BSMDB-2, 65-BSMDB-3
65-BSMDB-2 | KT | SMDB | L65 | 2 | Residential Group 4 Level 65 | 65-BSMDB-1 | METER
65-BSMDB-3 | KT | SMDB | L65 | 3 | Residential Group 4 Level 65 | 65-BSMDB-1 | METER
64-BSMDB-1 | KT | SMDB | L64 | 1 | Residential Group 4 Level 64 | 400A CB | METER, 64-PDB-1, 64-BSMDB-2, 64-BSMDB-3
64-BSMDB-2 | KT | SMDB | L64 | 2 | Residential Group 4 Level 64 | 64-BSMDB-1 | METER
64-BSMDB-3 | KT | SMDB | L64 | 3 | Residential Group 4 Level 64 | 64-BSMDB-1 | METER
63-BSMDB-1 | KT | SMDB | L63 | 1 | Residential Group 4 Level 63 | 400A CB | METER, 63-PDB-1, 63-BSMDB-2, 63-BSMDB-3
63-BSMDB-2 | KT | SMDB | L63 | 2 | Residential Group 4 Level 63 | 63-BSMDB-1 | METER
63-BSMDB-3 | KT | SMDB | L63 | 3 | Residential Group 4 Level 63 | 63-BSMDB-1 | METER
62-BSMDB-1 | KT | SMDB | L62 | 1 | Residential Group 4 Level 62 | 400A CB | METER, 62-PDB-1, 62-BSMDB-2, 62-BSMDB-3
62-BSMDB-2 | KT | SMDB | L62 | 2 | Residential Group 4 Level 62 | 62-BSMDB-1 | METER
62-BSMDB-3 | KT | SMDB | L62 | 3 | Residential Group 4 Level 62 | 62-BSMDB-1 | METER
61-BSMDB-1 | KT | SMDB | L61 | 1 | Residential Group 4 Level 61 | 400A CB | METER, 61-PDB-1, 61-BSMDB-2, 61-BSMDB-3
61-BSMDB-2 | KT | SMDB | L61 | 2 | Residential Group 4 Level 61 | 61-BSMDB-1 | METER
61-BSMDB-3 | KT | SMDB | L61 | 3 | Residential Group 4 Level 61 | 61-BSMDB-1 | METER
60-BSMDB-1 | KT | SMDB | L60 | 1 | Residential Group 4 Level 60 | 400A CB | METER, 60-PDB-1, 60-BSMDB-2, 60-BSMDB-3
60-BSMDB-2 | KT | SMDB | L60 | 2 | Residential Group 4 Level 60 | 60-BSMDB-1 | METER
60-BSMDB-3 | KT | SMDB | L60 | 3 | Residential Group 4 Level 60 | 60-BSMDB-1 | METER
59-BSMDB-1 | KT | SMDB | L59 | 1 | Residential Group 4 Level 59 | 400A CB | METER, 59-PDB-1, 59-BSMDB-2, 59-BSMDB-3
59-BSMDB-2 | KT | SMDB | L59 | 2 | Residential Group 4 Level 59 | 59-BSMDB-1 | METER
59-BSMDB-3 | KT | SMDB | L59 | 3 | Residential Group 4 Level 59 | 59-BSMDB-1 | METER
58-BSMDB-1 | KT | SMDB | L58 | 1 | Residential Group 4 Level 58 | 400A CB | METER, 58-PDB-1, 58-BSMDB-2, 58-BSMDB-3
58-BSMDB-2 | KT | SMDB | L58 | 2 | Residential Group 4 Level 58 | 58-BSMDB-1 | METER
58-BSMDB-3 | KT | SMDB | L58 | 3 | Residential Group 4 Level 58 | 58-BSMDB-1 | METER
68-MSMDB-C1 | KT | SMDB | L68 | 1 | MEP Level 68 | 69-LVSG-1B | VFD CHWP (68-1, 68-2, 68-3), CB CHWP-68-5, CB WH-4, 68-MDB-C1, 68-MDB-C2
68-MSMDB-B2 | KT | SMDB | L68 | 2 | MEP Level 68 | 69-LVSG-2A | 68-MDB-A1, 68-MDB-A2, 68-MDB-B1, 68-MDB-B2, 2 NOS CB WH-4
69-ESMDB-B2 | KT | SMDB | L71 | 1 | Refuge Area Level 71 | 69-LVSG-2B | 69-ATS-5, 69-ATS-4
69-MSMDB-B1 | KT | SMDB | L69 | 1 | MEP Level 69 | 69-LVSG-2B | 69-MSMDB-A1, 69-MDB-B1, 9-MDB-B2, 9-MDB-C1
69-MSMDB-A1 | KT | SMDB | L69 | 2 | MEP Level 69 | 69-MSMDB-B1 | VFD CHWP (69-1, 69-2, 69-3), 69-MDB-A1, 69-MDB-A2
73-BSMDB-1 | KT | SMDB | L73 | 1 | Residential Group 2 Level 73 | 250A CB | METER, 73-PDB-1
74-BSMDB-1 | KT | SMDB | L74 | 1 | Residential Group 2 Level 74 | 300A CB | METER, 74-PDB-1
74-BSMDB-2 | KT | SMDB | L74 | 2 | Residential Group 2 Level 74 | 74-BSMDB-1 | METER
75-BSMDB-1 | KT | SMDB | L75 | 1 | Residential Group 2 Level 75 | 250A CB | METER, 75-PDB-1
75-BSMDB-2 | KT | SMDB | L75 | 2 | Residential Group 2 Level 75 | 75-BSMDB-1 | METER
76-BSMDB-1 | KT | SMDB | L76 | 1 | Residential Group 2 Level 76 | 300A CB | METER, 76-PDB-1
76-BSMDB-2 | KT | SMDB | L76 | 2 | Residential Group 2 Level 76 | 76-BSMDB-1 | METER
77-BSMDB-1 | KT | SMDB | L77 | 1 | Residential Group 2 Level 77 | 250A CB | METER, 77-PDB-1
77-BSMDB-2 | KT | SMDB | L77 | 2 | Residential Group 2 Level 77 | 77-BSMDB-1 | METER
78-BSMDB-1 | KT | SMDB | L78 | 1 | Residential Group 2 Level 78 | 300A CB | METER, 78-PDB-1
78-BSMDB-2 | KT | SMDB | L78 | 2 | Residential Group 2 Level 78 | 78-BSMDB-1 | METER
79-BSMDB-1 | KT | SMDB | L79 | 1 | Residential Group 2 Level 79 | 250A CB | METER, 79-PDB-1
79-BSMDB-2 | KT | SMDB | L79 | 2 | Residential Group 2 Level 79 | 79-BSMDB-1 | METER
80-BSMDB-1 | KT | SMDB | L80 | 1 | Residential Group 2 Level 80 | 250A CB | METER, 80-PDB-1
80-BSMDB-2 | KT | SMDB | L80 | 2 | Residential Group 2 Level 80 | 80-BSMDB-1 | METER
81-BSMDB-1 | KT | SMDB | L81 | 1 | Residential Group 2 Level 81 | 300A CB | METER, 81-PDB-1
81-BSMDB-2 | KT | SMDB | L81 | 2 | Residential Group 2 Level 81 | 81-BSMDB-1 | METER
82-BSMDB-1 | KT | SMDB | L82 | 1 | Residential Group 2 Level 82 | 250A CB | METER, 82-PDB-1
82-BSMDB-2 | KT | SMDB | L82 | 2 | Residential Group 2 Level 82 | 82-BSMDB-1 | METER
83-BSMDB-1 | KT | SMDB | L83 | 1 | Residential Group 2 Level 83 | 300A CB | METER, 83-PDB-1
83-BSMDB-2 | KT | SMDB | L83 | 2 | Residential Group 2 Level 83 | 83-BSMDB-1 | METER
84-BSMDB-1 | KT | SMDB | L84 | 1 | Sky Lobby Level 84 | 300A CB | 84-PDB-1, 84-PDB-2, 84-PDB-3, 84-PDB-4
40-MSMDB-B1 | KT | SMDB | L40 | 1 | MEP Level 40 | 40-LVSG-1A | 40-MDB-A1, 40-MDB-A2, 40-MDB-B1, 40-MDB-B2, 40-PDB-1, 40-MSMDB-C1
40-MSMDB-C1 | KT | SMDB | L40 | 2 | MEP Level 40 | 40-MSMDB-B1 | VFD CHWP (40-1, 40-2, 40-3, 40-4, 40-5, 40-6), 40-MDB-C1, 40-MDB-C2
42-BSMDB-1 | KT | SMDB | L42 | 1 | Sky Lobby Level 42 | 400A CB | 42-PDB-1, 42-PDB-2, 42-PDB-3, 42-PDB-4, 42-PDB-5, 42-PDB-6,
43-BSMD-1 | KT | SMDB | L43 | 1 | Sky Lobby Level 43 | 400A CB | METER, 43-PDB-1, 43-BSMDB-2, 43-BSMDB-3
43-BSMD-2 | KT | SMDB | L43 | 2 | Sky Lobby Level 43 | 43-BSMD-1 | METER, 43-PDB-2
43-BSMD-3 | KT | SMDB | L43 | 3 | Sky Lobby Level 43 | 43-BSMD-1 | METER, 43-PDB-3
44-BSMDB-1 | KT | SMDB | L44 | 1 | Residential Group 1 Level 44 | 250A CB | METER, 44-PDB-1, 44-BSMDB-2, 44-BSMDB-3
44-BSMDB-2 | KT | SMDB | L44 | 2 | Residential Group 1 Level 44 | 44-BSMDB-1 | METER
44-BSMDB-3 | KT | SMDB | L44 | 3 | Residential Group 1 Level 44 | 44-BSMDB-1 | METER
45-BSMDB-1 | KT | SMDB | L45 | 1 | Residential Group 1 Level 45 | 250A CB | METER, 45-PDB-1, 45-BSMDB-2, 45-BSMDB-3
45-BSMDB-2 | KT | SMDB | L45 | 2 | Residential Group 1 Level 45 | 45-BSMDB-1 | METER
45-BSMDB-3 | KT | SMDB | L45 | 3 | Residential Group 1 Level 45 | 45-BSMDB-1 | METER
46-BSMDB-1 | KT | SMDB | L46 | 1 | Residential Group 1 Level 46 | 250A CB | METER, 46-PDB-1, 46-BSMDB-2, 46-BSMDB-3
46-BSMDB-2 | KT | SMDB | L46 | 2 | Residential Group 1 Level 46 | 46-BSMDB-1 | METER
46-BSMDB-3 | KT | SMDB | L46 | 3 | Residential Group 1 Level 46 | 46-BSMDB-1 | METER
47-BSMDB-1 | KT | SMDB | L47 | 1 | Residential Group 1 Level 47 | 250A CB | METER, 47-PDB-1, 47-BSMDB-2, 47-BSMDB-3
47-BSMDB-2 | KT | SMDB | L47 | 2 | Residential Group 1 Level 47 | 47-BSMDB-1 | METER
47-BSMDB-3 | KT | SMDB | L47 | 3 | Residential Group 1 Level 47 | 47-BSMDB-1 | METER
48-BSMDB-1 | KT | SMDB | L48 | 1 | Residential Group 1 Level 48 | 250A CB | METER, 48-PDB-1, 48-BSMDB-2, 48-BSMDB-3
48-BSMDB-2 | KT | SMDB | L48 | 2 | Residential Group 1 Level 48 | 48-BSMDB-1 | METER
48-BSMDB-3 | KT | SMDB | L48 | 3 | Residential Group 1 Level 48 | 48-BSMDB-1 | METER
49-BSMDB-1 | KT | SMDB | L49 | 1 | Residential Group 1 Level 49 | 250A CB | METER, 49-PDB-1, 49-BSMDB-2, 49-BSMDB-3
49-BSMDB-2 | KT | SMDB | L49 | 2 | Residential Group 1 Level 49 | 49-BSMDB-1 | METER
49-BSMDB-3 | KT | SMDB | L49 | 3 | Residential Group 1 Level 49 | 49-BSMDB-1 | METER
50-BSMDB-1 | KT | SMDB | L50 | 1 | Residential Group 1 Level 50 | 250A CB | METER, 50-PDB-1, 50-BSMDB-2, 50-BSMDB-3
50-BSMDB-2 | KT | SMDB | L50 | 2 | Residential Group 1 Level 50 | 50-BSMDB-1 | METER
50-BSMDB-3 | KT | SMDB | L50 | 3 | Residential Group 1 Level 50 | 50-BSMDB-1 | METER
51-BSMDB-1 | KT | SMDB | L51 | 1 | Residential Group 1 Level 51 | 250A CB | METER, 51-PDB-1, 51-BSMDB-2, 51-BSMDB-3
51-BSMDB-2 | KT | SMDB | L51 | 2 | Residential Group 1 Level 51 | 51-BSMDB-1 | METER
51-BSMDB-3 | KT | SMDB | L51 | 3 | Residential Group 1 Level 51 | 51-BSMDB-1 | METER
52-BSMDB-1 | KT | SMDB | L52 | 1 | Residential Group 1 Level 52 | 250A CB | METER, 52-PDB-1, 52-BSMDB-2, 52-BSMDB-3
52-BSMDB-2 | KT | SMDB | L52 | 2 | Residential Group 1 Level 52 | 52-BSMDB-1 | METER
52-BSMDB-3 | KT | SMDB | L52 | 3 | Residential Group 1 Level 52 | 52-BSMDB-1 | METER
53-BSMDB-1 | KT | SMDB | L53 | 1 | Residential Group 1 Level 53 | 250A CB | METER, 53-PDB-1, 53-BSMDB-2, 53-BSMDB-3
53-BSMDB-2 | KT | SMDB | L53 | 2 | Residential Group 1 Level 53 | 53-BSMDB-1 | METER
53-BSMDB-3 | KT | SMDB | L53 | 3 | Residential Group 1 Level 53 | 53-BSMDB-1 | METER
54-BSMDB-1 | KT | SMDB | L54 | 1 | Residential Group 1 Level 54 | 250A CB | METER, 54-PDB-1, 54-BSMDB-2, 54-BSMDB-3
54-BSMDB-2 | KT | SMDB | L54 | 2 | Residential Group 1 Level 54 | 54-BSMDB-1 | METER
54-BSMDB-3 | KT | SMDB | L54 | 3 | Residential Group 1 Level 54 | 54-BSMDB-1 | METER
55-BSMDB-1 | KT | SMDB | L55 | 1 | Residential Group 1 Level 55 | 250A CB | METER, 55-PDB-1, 55-BSMDB-2, 55-BSMDB-3
55-BSMDB-2 | KT | SMDB | L55 | 2 | Residential Group 1 Level 55 | 55-BSMDB-1 | METER
55-BSMDB-3 | KT | SMDB | L55 | 3 | Residential Group 1 Level 55 | 55-BSMDB-1 | METER
39-MSMDB-A1 | KT | SMDB | L39 | 1 | MEP Level 39 | 40-LVSG-2A | VFD CHWP (39-1, 39-2, 38-6, 39-7, 39-11, 39-12), 39-MDB-A1
39-MSMDB-A2 | KT | SMDB | L39 | 2 | MEP Level 39 | 40-LVSG-2A | CFD CHWP (39-3, 39-4, 39-5, 39-13), 39-MDB-A1
39-MSMDB-C1 | KT | SMDB | L39 | 3 | MEP Level 39 | 40-LVSG-2B | CB WH-3-1, CB WH-3-2
39-MSMDB-B1 | KT | SMDB | L39 | 4 | MEP Level 39 | 40-LVSG-2B | 39-MDB-B1, 39-MDB-B2, 39-PDB-1, CB WH-3-3
40-MSMDB-B2 | KT | SMDB | L40 | 3 | MEP Level 40 | 40-LVSG-2B | 40-ATS-4, 40-ATS-5
162-ESMDB-3 | KT | SMDB | L162 | 6 | MEP Level 162 | 162-EM-LVSG-1 | 162-ATS-3, 162-ATS-2
162-CSMDB-1 | KT | SMDB | L162 | 7 | MEP Level 162 | 162-ATS-3 | 154-CDB-1, 162-CDB-1, 168-CDB-1, 184-CDB-1, 203-CDB-1, 222-CDB-1
162-ELSMDB-1 | KT | SMDB | L162 | 8 | MEP Level 162 | 162-ATS-2 | 162-ELSMDB-2, 162-CBSMDB-1
162-ELSMDB-2 | KT | SMDB | L162 | 9 | MEP Level 162 | 162-ELSMDB-1 | 154-ELDB-1, 158-ELDB-1, 162-ELDB-1, 168-ELDB-1, 184-ELDB-1, 203-ELDB-1, 222-ELDB-1
162-CBSMDB-1 | KT | SMDB | L162 | 10 | MEP Level 162 | 162-ELSMDB-1 | 154-CBS-1, 161-CBS-1, 168-CBS-1, 184-CBS-1, 203-CBS-1, 222-CBS-1
162-ESMDB-1 | KT | SMDB | L162 | 11 | MEP Level 162 | 162-ATS-1 | CB 168 (BME-1, BME-2, BME-3), VFD CH-168-1, 162-EMDB-1, 161-EMDB-1, 161-EMDB-2, 159-EMDB-1
162-ESMDB-2 | KT | SMDB | L162 | 12 | MEP Level 162 | 162-ATS-4 | 164-EMDB-1, 165-EMDB-1, 169-EMDB-1, 184-EMDB-1, 203-EMDB-1, 222-EMDB-1, 155-ESMDB-1
155-ESMDB-1 | KT | SMDB | L155 | 2 | BMU/MEP Level 155 | 162-ESMDB-2 | CB 156 (BME-1, BME-2), VFD CHWP (155-1, 155-5), 155-EMDB-1, 154-EMDB-1
162-EBVSMDB-1 | KT | SMDB | L162 | 13 | MEP Level 162 | 162-EM-LVSG-1 | 162-ATS-5, 162-ATS-6
162-EVSMDB-1 | KT | SMDB | L162 | 14 | MEP Level 162 | 162-ATS-5 | CB ELEVATORS (OB1, OB2), 162-EVDB-1, CB ELEVATORS (OR1, OR2), 161-EVDB-1
171-EVSMDB-1 | KT | SMDB | L171 | 1 | TMD Reserve Level 171 | 162-ATS-6 | CB ELEVATOR S3, 171-EVDB-1, CB ELEVATOR FS2, 171-EVDB-2, CB ELEVATOR WL1, 170-EVSB-1
88/89-EVSMDB-1 | KT | SMDB | L88 | 3 | Residential Group 3A Level 88 | 88/89-ATS-1 | CB ELEVATOR (RS4, RS-5, RS-6), 88/89-EVDB-1
95-ESMDB-1 | KT | SMDB | L95 | 3 | MEP Level 95 | 95-ATS-1 | CONTROLLER (3NOS. BP-10, 3NOS. BP-9), VFD CHWP (95-6, 95-7, 95-8), VFD AHU 95-C, 95-EMDB-1, 95-EMDB-2, 86-EMDB-1, 84-EMDB-1
96-ESMDB-1 | KT | SMDB | L96 | 2 | MEP Level 96 | 96-EM-LVSG-1 | 96-ATS-2, 96-ATS-4, 96-ATS-5
96-ESMDB-A1 | KT | SMDB | L96 | 3 | MEP Level 96 | 96-ATS-2 | 96-EMDB-A1, 96-EMDB-C1, 104-EMDB-1, VFD CHWP (96-4, 96-C)
96-CSMDB-1 | KT | SMDB | L96 | 4 | MEP Level 96 | 96-ATS-4 | 86-CDB-1, 87-CDB-1, 93-CDB-1, 96-CDB-1, 102-CDB-1, 104-CDB-1, UPS 80KVA NETPOP "C"
96-ELSMDB-1 | KT | SMDB | L96 | 5 | MEP Level 96 | 96-ATS-5 | 96-ELSMDB-2, 96-CBSMDB-1
96-ELSMDB-2 | KT | SMDB | L96 | 6 | MEP Level 96 | 96-ELSMDB-1 | 86-ELDB-1, 89-ELDB-1, 94-ELDB-1, 100-ELDB-1, 104-ELDB-1
96-CBSMDB-1 | KT | SMDB | L96 | 7 | MEP Level 96 | 96-ELSMDB-1 | 86-CBS-1, 88-CBS-1, 91-CBS-1, 95-CBS-1, 101-CBS-1, 104-CBS-1
85-EVSMDB-1 | KT | SMDB | L85 | 1 | Sky Lobby Level 85 | 95/96-ATS-6 | CB ELEVATOR (R4, R5, R6) 85-EVDB-1
121-EVSMDB-1 | KT | SMDB | L121 | 4 | MEP Level 121 | 121/122-ATS-3 | CB ELEVATOR (R7, R8, R9), 121-EVDB-1
122-ESMDB-B1 | KT | SMDB | L122 | 2 | MEP Level 122 | 122-EM-LVSG-1 | 122-ATS-2, 121-ATS-1
122-ESMDB-B2 | KT | SMDB | L122 | 3 | MEP Level 122 | 122-ATS-2 | CB (BME-1, BME-2, BME-3), VFD AHU-122-C, 122-EMDB-A1, 122-EMDB-B1, 124-EMDB-1
121-ESMDB-1 | KT | SMDB | L121 | 5 | MEP Level 121 | 121-ATS-1 | CONTROLLER (4NOS. BP-11, 4NOS. BP-12), 121-EMDB-A1, 121-EMDB-C1
122-ESMDB-2 | KT | SMDB | L122 | 4 | MEP Level 122 | 122-EM-LVSG-1 | 122-ATS-5, 122-ATS-4
122-ELSMDB-1 | KT | SMDB | L122 | 5 | MEP Level 122 | 122-ATS-5 | 122-CBSMDB-1, 122-ELSMDB-2
122-CBSMDB-1 | KT | SMDB | L122 | 6 | MEP Level 122 | 122-ELSMDB-1 | 107-CBS-1, 111-CBS-1, 115-CBS-1, 121-CBS-1, 124-CBS-1
122-ELSMDB-2 | KT | SMDB | L122 | 7 | MEP Level 122 | 122-ELSMDB-1 | 108-ELDB-1, 116-ELDB-1, 120-ELDB-1, 124-ELDB-1
122-CSMDB-1 | KT | SMDB | L122 | 8 | MEP Level 122 | 122-ATS-4 | 106-CDB-1, 110-CDB-1, 114-CDB-1, 118-CDB-1, 124-CDB-1
140-ESMDB-1 | KT | SMDB | L140 | 1 | Void Level 140 | 140-EM-LVSG-1 | 140-ATS-3, 140-ATS-2
140-CSMDB-1 | KT | SMDB | L140 | 2 | Void Level 140 | 140-ATS-3 | 132-CDB-1, 140-CDB-1, 148-CDB-1
140-ELSMDB-1 | KT | SMDB | L140 | 3 | Void Level 140 | 140-ATS-2 | 140-ELSMDB-2, 140-CBSMDB-1
140-ELSMDB-2 | KT | SMDB | L140 | 4 | Void Level 140 | 140-ELSMDB-1 | 132-ELDB-1, 140-ELDB-1, 148-ELDB-1
140-CBSMDB-1 | KT | SMDB | L140 | 5 | Void Level 140 | 140-ELSMDB-1 | 130-CBS-1, 138-CBS-1, 146-CBS-1
140-ESMDB-2 | KT | SMDB | L140 | 6 | Void Level 140 | 140-ATS-1 | 140-EMDB-1, 144-EMDB-1, 146-ESMDB-1
146-ESMDB-1 | KT | SMDB | L146 | 1 | Level 146 | 140-ESMDB-2 | VFD AHU (146-1, 146-2), CONTROLLER (3NOS. BP-13), 146-EMDB-1, 146-EMDB-2
39-EBVSMDB-1 | KT | SMDB | L39 | 5 | MEP Level 39 | 39-ATS-3 | 28/29-EVSMDB-1, 39-EVSMDB-1, 39-EVSMDB-2
28/29-EVSMDB-1 | KT | SMDB | L28 | 4 | Service Apartments Level 28 | 39-EBVSMDB-1 | CB ELEVATOR (H1, H2, H3), 28/29-EVDB-1
39-EVSMDB-1 | KT | SMDB | L39 | 6 | MEP Level 39 | 39-EBVSMDB-1 | CB ELEVATOR (HS1, HS2), 39-EVDB-1
39-EVSMDB-2 | KT | SMDB | L39 | 6 | MEP Level 39 | 39-EBVSMDB-1 | CB ELEVATOR (A1, A2, A3), 39-EVDB-2
40-ESMDB-B1-1 | KT | SMDB | L40 | 4 | MEP Level 40 | 40-ATS-B1 | VFD AHU (40-1, 40-C), 40-EMDB-A1 40-EMDB-B1, 40-EMDB-C1, 56-EMDB-1, 58-EMDB-1
46-EVSMDB-1 | KT | SMDB | L46 | 4 | Residential Group 1 Level 46 | 46-ATS-1 | CB ELEVATOR (RS-1, RS-2, RS-3) 46-EVDB-1
40-ESMDB-B1-2 | KT | SMDB | L40 | 5 | MEP Level 40 | 40-EM-LVSG-1 | 40-CSMDB-B1 & 40-ELSMDB-B1
40-CSMDB-B1 | KT | SMDB | L40 | 6 | MEP Level 40 | 40-ESMDB-B1-2 | 30-CDB-1, 34-CDB-1, 38-CDB-1, 42-CDB-1, 46-CDB-1, 50-CDB-1, 54-CDB-1, 56-CDB-1
40-ELSMDB-B1 | KT | SMDB | L40 | 7 | MEP Level 40 | 40-ESMDB-B1-2 | 40-ELSMDB-B2, 40-CBSMDB-B1
40-ELSMDB-B2 | KT | SMDB | L40 | 8 | MEP Level 40 | 40-ELSMDB-B1 | 29-ELDB-1, 35-ELDB-1, 38-ELDB-1, 40-ELDB-1, 46-ELDB-1, 54-ELDB-1, 56-ELDB-1
40-CBSMDB-B1 | KT | SMDB | L40 | 9 | MEP Level 40 | 40-ELSMDB-B1 | 28-CBS-1, 31-CBS-1, 34-CBS-1, 38-CBS-1, 40-CBS-1, 44-CBS-1, 47-CBS-1, 50-CBS-1, 53-CBS-1, 56-CBS-1
69-EBVSMDB-1 | KT | SMDB | L69 | 3 | MEP Level 69 | 69-ATS-3 | 71-EVSMDB-1, 69-EVSMDB-2
71-EVSMDB-1 | KT | SMDB | L71 | 2 | Refuge Area Level 71 | 69-EBVSMDB-1 | CB ELEVATOR FS1, 71-EVDB-1
69-EVSMDB-2 | KT | SMDB | L69 | 4 | MEP Level 69 | 69-EBVSMDB-1 | CB ELEVATOR (R1, R2, R3), 69-EVDB-2
69-ESMDB-B1 | KT | SMDB | L69 | 5 | MEP Level 69 | 69-ATS-2 | VFD (AHU-69-C, CHWP-69-4), CB BME (69-1, 69-2, 69-3), 69-EMDB-A1, 69-EMDB-B1, 71-EMDB-1
68-ESMDB-B1 | KT | SMDB | L68 | 3 | MEP Level 68 | 68-ATS-1 | VFD AHU-68-C, CONTROLLER (3NOS. BP7, 3NOS. BP-8), 68-EMDB-A1, 68-EMDB-B1, 68-EMDB-B2, 68-EMDB-C1
71-EVSMDB-3 | KT | SMDB | L71 | 3 | Refuge Area Level 71 | 69-EM-LVSG-1 | CB ELEVATOR (S1, S2)
69-ESMDB-B3 | KT | SMDB | L69 | 6 | MEP Level 69 | 69-EM-LVSG-1 | 69-ATS-4, 69-ATS-5
69-CSMDB-B1 | KT | SMDB | L69 | 7 | MEP Level 69 | 69-ATS-4 | 58-CDB-1, 62-CDB-1, 66-CDB-1, 71-CDB-1, 75-CDB-1, 78-CDB-1, 82-CDB-1
69-ELSMDB-B1 | KT | SMDB | L69 | 8 | MEP Level 69 | 69-ESMDB-B3 | 69-ELSMDB-B2, 69-CBSMDB-1
69-ELSMDB-B2 | KT | SMDB | L69 | 9 | MEP Level 69 | 69-ELSMDB-B1 | 60-ELDB-1, 65-ELDB-1, 71-ELDB-1, 76-ELDB-1, 81-ELDB-1
69-CBSMDB-1 | KT | SMDB | L69 | 10 | MEP Level 69 | 69-ELSMDB-B1 | 59-CBS-1, 63-CBS-1, 68-CBS-1, 71-CBS-1, 74-CBS-1, 77-CBS-1, 80-CBS-1, 83-CBS-1
B3-ESMDB-C2-1 | KT | SMDB | B3 | 1 | Parking/MEP Level B3 | B2-ATS-T1-1 | B3-EMDB-C1-1, B3-EMDB-C1-2, B3-EMDB-C1-3, B3-EMDB-C2-1, B3-EMDB-C2-2, B3-EMDB-C2-3, B3-EMDB-C2-4, VFD AHU (B3-H-1, B3-H-2)
B2-ESMDB-T1-1 | KT | SMDB | B2 | 11 | Parking/MEP Level B2 | B2-ATS-T1-2 | B2-EMDB-T1-1, B2-EMDB-C1-1, B1-EMDB-C1-1, B1-EMDB-C2-1, B1M-EMDB-T1-1
4-ESMDB-T1-1 | KT | SMDB | L4 | 2 | Spa Level 4 | B2-ATS-T1-3 | 4-EMDB-T1-1, 5-EMDB-T1-1, VFD AHU (4-H-1, 4-H-11, 4-1)
2-ESMDB-T1-1 | KT | SMDB | L2 | 2 | Lobby/Amenities Level 2 | B2-ATS-T1-4 | 2-EMDB-T1-1, 2-EMDB-T1-2, 2-EMDB-T1-3, 2M-EMDB-T1-1, 2M-EMDB-T1-2, 2M-EMDB-T1-3, VFD AHU (2-1, 2-2, 2-3)
15-ESMDB-B1 | KT | SMDB | L15 | 2 | MEP Level 15 | 15-ATS-B1 | 15-ELSMDB-B1, 15-CBSMDB-B1
15-ELSMDB-B1 | KT | SMDB | L15 | 3 | MEP Level 15 | 15-ESMDB-B1 | 9-ELDB-1, 13-ELDB-1, 18-ELDB-1, 23-ELDB-1
15-CBSMDB-B1 | KT | SMDB | L15 | 4 | MEP Level 15 | 15-ESMDB-B1 | 8-CBS-1, 11-CBS-1, 15-CBS-1, 18-CBS-1, 21-CBS-1, 24-CBS-1
15-CSMDB-B1 | KT | SMDB | L15 | 5 | MEP Level 15 | 15-ATS-B2 | 7-CDB-1, 9-CDB-1, 12-CDB-1, 13-CDB-1, 15-CDB-1, 16-CDB-1, 18-CDB-1, 22-CDB-1, 26-CDB-1, UPS 80KVA NETPOP "B"
15-EMSMDB-B1 | KT | SMDB | L15 | 6 | MEP Level 15 | 15-ATS-B3 | 15-ESMDB-A1, 15-ESMDB-B1
15-ESMDB-A1 | KT | SMDB | L15 | 7 | MEP Level 15 | 15-EMSMDB-B1 | VFD AHU (15-1, 15-6, 15-11, 15-12), 15-EMDB-A1, 15-EMDB-A2
15-ESMDB-B1 | KT | SMDB | L15 | 8 | MEP Level 15 | 15-EMSMDB-B1 | VFD AHU (15-5, 15-4, 15-2,), VFD RF (15-5, 15-4, 15-13), CB AHU 15-13, 15-EMDB-B1
15-EMSMDB-C1 | KT | SMDB | L15 | 9 | MEP Level 15 | 15-ATS-C | 15-ESMDB-C2, 15-ESMDB-C1
15-ESMDB-C2 | KT | SMDB | L15 | 10 | MEP Level 15 | 15-EMSMDB-C1 | VFD AHU (15-3, 15-7), VFD RF-15-3, CONTROLLER (4NOS. BP-3), CONTROLLER (4NOS. BP-4)
15-ESMDB-C1 | KT | SMDB | L15 | 11 | MEP Level 15 | 15-EMSMDB-C1 | VFD AHU (15-8, 15-9, 15-10, 15-C), VFD RF (15-8, 15-9, 15-10, 15-C), 15-EMDB-C1
16-ESMDB-B1 | KT | SMDB | L16 | 3 | MEP Level 16 | 16-ATS-B1 | VFD AHU (16-1, 16-2, 16-C), VFD CHWP-16-6, 16-EMDB-A1, 16-EMDB-B1, 16-EMDB-C1, 18-ESMDB-1
16-EBVSMDB-1 | KT | SMDB | L16 | 4 | MEP Level 16 | 16-ATS-2 | 16-EVSMDB-1, 16-EVSMDB-2
16-EVSMDB-1 | KT | SMDB | L16 | 5 | MEP Level 16 | 16-EBVSMDB-1 | CB ELEVATOR (O1 TO O5), 15-EVDB-1
16-EVSMDB-2 | KT | SMDB | L16 | 6 | MEP Level 16 | 16-EBVSMDB-1 | CB ELEVATOR OS1, 16-EVDB-2
39-ESMDB-C1 | KT | SMDB | L39 | 7 | MEP Level 39 | 39-ATS-C1 | 39-EMDB-C1, VFD AHU-39-C, CONTROLLER (5NOS. BP-5) & (5NOS. BP-6)
39-ESMDB-B2 | KT | SMDB | L39 | 8 | MEP Level 39 | 39-ATS-B1 | VFD CHWP (39-8, 39-9, 39-10), 39-EMDB-A1, 39-EMDB-A2, 39-EMDB-B1, 38-EMDB-1
B2-ESMDB-T1-2 | KT | SMDB | B2 | 12 | Parking/MEP Level B2 | B2-EM-LVSG-2 | B2-ATS-T1-5, B2-ATS-T1-6
B2-ELSMDB-T1-1 | KT | SMDB | B2 | 13 | Parking/MEP Level B2 | B2-ATS-T1-5 | B2-ELSMDB-T1-2, B2-CBSMDB-T1-1
B2-ELSMDB-T1-2 | KT | SMDB | B2 | 14 | Parking/MEP Level B2 | B2-ELSMDB-T1-1 | 4-ELDB-T1, 2-ELDB-T1, 1-ELDB-T1, B1M-ELDB-T1, B1-ELDB-T1, B2-ELDB-T1, B2-ELDB-C1, B2-ELDB-T2, B3-ELDB-C2
B2-CBSMDB-T1-1 | KT | SMDB | B2 | 15 | Parking/MEP Level B2 | B2-ELSMDB-T1-1 | 4-CBS-T1, 2-CBS-T1, 1-CBS-T1, B1M-CBS-T1, B1-CBS-T1, B2-CBS-T1, B2-CBS-C1, B2-CBS-T2, B3-CBS-C2
B2-CSMDB-T1-1 | KT | SMDB | B2 | 16 | Parking/MEP Level B2 | B2-ATS-T1-6 | B3-CDB-C1-1, B2-CDB-T1-1, B2-CDB-C1-1, B1-CDB-C1-1, B1-CDB-T1-1, B1M-CDB-T1-1, 2-CDB-T1-1, 4-CDB-T1-1, UPS 120KVA, UPS200KVA
2M-EBVSMDB-T1-1 | KT | SMDB | L2 | 3 | Lobby/Amenities Level 2 | B2-ATS-T1-7 | 2M-EVSMDB-T1-1, 2M-EVSMDB-T1-2, 2M-EVSMDB-T1-3
2M-EVSMDB-T1-1 | KT | SMDB | L2 | 4 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-1 | CB ELEVATOR (OP1, OP2, OP3, OP4), 2M-EVDB-T1-1
2M-EVSMDB-T1-2 | KT | SMDB | L2 | 5 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-1 | CB ELEVATOR (AP1, AP2), 2M-EVDB-T1-2
2M-EVSMDB-T1-3 | KT | SMDB | L2 | 6 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-1 | CB ELEVATOR (RP1, RP2, RP3, RP4), 2M-EVDB-T1-3
2M-EBVSMDB-T1-2 | KT | SMDB | L2 | 7 | Lobby/Amenities Level 2 | B2-ATS-T1-8 | 2M-EVSMDB-T1-4, 2M-EVSMDB-T1-5, 2-EVSMDB-T1-1
2M-EVSMDB-T1-4 | KT | SMDB | L2 | 8 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-2 | CB ELEVATOR (HP1, HP2), 2M-EVDB-T1-4
2M-EVSMDB-T1-5 | KT | SMDB | L2 | 9 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-2 | CB ELEVATOR (HS3, HS4, HS5, HS6, HS7), 2M-EVDB-T1-5
2-EVSMDB-T1-1 | KT | SMDB | L2 | 10 | Lobby/Amenities Level 2 | 2M-EBVSMDB-T1-2 | CB ELEVATOR (B1, B2), 2-EVDB-T1-1
B1-ESMDB-B1-1 | KT | SMDB | B1 | 12 | Parking Level B1 | B1-ATS-B1-1 | B1-EMDB-B1-1, B1-EMDB-B1-2, B1-EMDB-B1-3, B1-EMDB-B2-1, B1-EMDB-B2-2
B3-ESMDB-N-1 | KT | SMDB | B3 | 2 | Parking/MEP Level B3 | B1-ATS-N-3 | CONTROLLER (5NOS. BP-1, 5NOS. BP-2), B3-EMDB-N1, B3-EMDB-N2, B3-EMDB-N3
B3-ESMDB-A1-1 | KT | SMDB | B3 | 3 | Parking/MEP Level B3 | B1-ATS-N-4 | B3-EMDB-A1-1, B3-EMDB-A1-2, B3-EMDB-A1-3, B3-EMDB-A2-1, B3-EMDB-A2-2, B3-EMDB-A2-3, B3-EMDB-A2-4
B2-ESMDB-A1-1 | KT | SMDB | B2 | 17 | Parking/MEP Level B2 | B1-ATS-N-1 | B2-EMDB-A2-1, B2-EMDB-A2-2, B2-EMDB-A2-3
B1-ESMDB-A1-4 | KT | SMDB | B1 | 13 | Parking Level B1 | B1-ATS-N-2 | B1-EMDB-A1-1, B1-EMDB-A1-2, B1-EMDB-A1-3, VFD AHU-B1-H-3, VFD CHWP (B1-12, B1-22)
B1-ESMDB-A2-5 | KT | SMDB | B1 | 14 | Parking Level B1 | B1-ATS-N-8 | B1-EMDB-A2-1, B1-EMDB-A2-2, B1-EMDB-A2-3, VFD CHWP (B1-5, B1-6, B1-11)
B1-ESMDB-A1-1 | KT | SMDB | B1 | 15 | Parking Level B1 | B1-ATS-N-7 | VFD EGF (B1-1 TO B1-8), VFD LDEF-B1-1
B1-ESMDB-N-2 | KT | SMDB | B1 | 16 | Parking Level B1 | B1-EM-LVSG-2 | B1-ATS-N-5, B1-ATS-N-6
B1-CSMDB-N-1 | KT | SMDB | B1 | 17 | Parking Level B1 | B1-ATS-N-5 | B3-CDB-A2-1, B2-CDB-A2-1, B1-CDB-A2-1, B1M-CDB-A2-1, 1-CDB-NG-1, UPS 80KVA, UPS 30KVA, UPS 100KVA
B1-ELSMDB-N-1 | KT | SMDB | B1 | 18 | Parking Level B1 | B1-ATS-N-6 | B1-ELSMDB-N-2, B1-CBSMDB-N-1
B1-ELSMDB-N-2 | KT | SMDB | B1 | 19 | Parking Level B1 | B1-ELSMDB-N-1 | B1-ELDB-N, B2-ELDB-A2, B3-ELDB-A1
B1-CBSMDB-N-1 | KT | SMDB | B1 | 20 | Parking Level B1 | B1-ELSMDB-N-1 | B3-CBS-A1,B2-CBS-A2, B1-CBS-N1, 1-CBS-NG-1
B2-ESMDB-S-1 | KT | SMDB | B2 | 18 | Parking/MEP Level B2 | B2-EM-LVSG-3 | B2-ATS-S-6, B1-ATS-S-2
B2-ESMDB-B1-1 | KT | SMDB | B2 | 19 | Parking/MEP Level B2 | B2-ATS-S-6 | VFD EGF (B2-1 TO B2-8)
B1-ESMDB-B1-1 | KT | SMDB | B1 | 21 | Parking Level B1 | B1-ATS-S-2 | VFD AHU-B1-H-8, VFD LDEF-B1-2, VFD LDSF-B1-1
B3-ESMDB-B1-1 | KT | SMDB | B3 | 4 | Parking/MEP Level B3 | B3-ATS-S-1 | B3-EMDB-B1-1, B3-EMDB-B1-2, B3-EMDB-B1-3, B3-EMDB-B1-4, B3-EMDB-B1-5
B3-ESMDB-B2-1 | KT | SMDB | B3 | 5 | Parking/MEP Level B3 | B3-ATS-S-2 | B3-EMDB-B2-1, B3-EMDB-B2-2, B3-EMDB-B2-3, B3-EMDB-B2-4
B2-ESMDB-B2-2 | KT | SMDB | B2 | 20 | Parking/MEP Level B2 | B2-ATS-S-9 | B2-EMDB-B1-1, B2-EMDB-B1-2, B2-EMDB-B1-3, B2-EMDB-B2-1, B2-EMDB-B2-2
B2-EMSMDB-S-3 | KT | SMDB | B2 | 21 | Parking/MEP Level B2 | B2-EM-LVSG-3 | B2-ATS-S-7, B2-ATS-S-8
B2-CSMDB-S-1 | KT | SMDB | B2 | 22 | Parking/MEP Level B2 | B2-ATS-S-7 | B3-CDB-B1, B2-CDB-B1, B2-CDB-SG-1, B1M-CDB-B1, 1-CDB-SG-1, UPS 80KVA, UPS 30KVA
B2-ELSMDB-S-1 | KT | SMDB | B2 | 23 | Parking/MEP Level B2 | B2-ATS-S-8 | B2-ELSMDB-S-2, B2-CBSMDB-S-1
B2-ELSMDB-S-2 | KT | SMDB | B2 | 24 | Parking/MEP Level B2 | B2-ELSMDB-S-1 | B2-ELDB-B1, B2-ELDB-B2, B2-ELDB-S
B2-CBSMDB-S-1 | KT | SMDB | B2 | 25 | Parking/MEP Level B2 | B2-ELSMDB-S-1 | B2-CBS-B1, B2-CBS-B2, B2-CBS-S, 1-CBS-SG-1
VFD MAU-16-2 | KT | VFD | L16 | 1 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | MAU-16-2
VFD RF-16-2 | KT | VFD | L16 | 2 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | RF-16-2
VFD CHWP-16-1 | KT | VFD | L16 | 3 | Electrical Plants at Level 15/16 | 16-MSMDB-C1 | CHWP-16-1
VFD CHWP-16-2 | KT | VFD | L16 | 4 | Electrical Plants at Level 15/16 | 16-MSMDB-C1 | CHWP-16-2
VFD CHWP-16-3 (STAND-BY) | KT | VFD | L16 | 5 | Electrical Plants at Level 15/16 | 16-MSMDB-C1 | CHWP-16-3
VFD CHWP-15-1 | KT | VFD | L15 | 1 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | CHWP-15-1
VFD CHWP-15-2 | KT | VFD | L15 | 2 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | CHWP-15-2
VFD CHWP-B1-1 | KT | VFD | B1 | 1 | Parking Level B1 | B1-MSMDB-N-2 | CHWP-B1-1
VFD CHWP-B1-2 | KT | VFD | B1 | 2 | Parking Level B1 | B1-MSMDB-N-2 | CHWP-B1-2
VFD CHWP-B1-3 | KT | VFD | B1 | 3 | Parking Level B1 | B1-MSMDB-N-2 | CHWP-B1-3
VFD CHWP-B1-4 | KT | VFD | B1 | 4 | Parking Level B1 | B1-MSMDB-N-2 | CHWP-B1-4
VFD CHWP-B1-7 | KT | VFD | B1 | 5 | Parking Level B1 | B1-MSMDB-N-2 | CHWP-B1-7
VFD CHWP-B1-8 | KT | VFD | B1 | 6 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-8
VFD CHWP-B1-9 | KT | VFD | B1 | 7 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-9
VFD CHWP-B1-10 | KT | VFD | B1 | 8 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-10
VFD CHWP-B1-19 | KT | VFD | B1 | 9 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-19
VFD CHWP-B1-20 | KT | VFD | B1 | 10 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-20
VFD CHWP-B1-21 | KT | VFD | B1 | 11 | Parking Level B1 | B1-MSMDB-N-1 | CHWP-B1-21
VFD TTEF-B1-1 | KT | VFD | B1 | 12 | Parking Level B1 | B1-MSMDB-B1-1 | TTEF-B1-1
VFD TTEF-B1-2 | KT | VFD | B1 | 13 | Parking Level B1 | B1-MSMDB-B1-1 | TTEF-B1-2
VFD TTEF-B1-3 | KT | VFD | B1 | 14 | Parking Level B1 | B1-MSMDB-B1-1 | TTEF-B1-3
VFD TTEF-B1-4 | KT | VFD | B1 | 15 | Parking Level B1 | B1-MSMDB-B1-1 | TTEF-B1-4
VFD TTEF-B1-5 | KT | VFD | B1 | 16 | Parking Level B1 | B1-MSMDB-B1-1 | TTEF-B1-5
VFD LDEF-B1-3 | KT | VFD | B1 | 17 | Parking Level B1 | B1-MSMDB-B1-1 | LDEF-B1-3
VFD LDEF-B1-4 | KT | VFD | B1 | 18 | Parking Level B1 | B1-MSMDB-B1-1 | LDEF-B1-4
VFD LDSF-B1-2 | KT | VFD | B1 | 19 | Parking Level B1 | B1-MSMDB-B1-1 | LDSF-B1-2
VFD AHU-161-1 | KT | VFD | L161 | 1 | MEP Level 161 | 162-MSMDB-3 | AHU-161-1
VFD AHU-161-2 | KT | VFD | L161 | 2 | MEP Level 161 | 162-MSMDB-3 | AHU-161-2
VFD AHU-161-3 | KT | VFD | L161 | 3 | MEP Level 161 | 162-MSMDB-3 | AHU-161-3
VFD CHWP-161-1 | KT | VFD | L161 | 4 | MEP Level 161 | 162-MSMDB-3 | CHWP-161-1
VFD CHWP-161-2 | KT | VFD | L161 | 5 | MEP Level 161 | 162-MSMDB-3 | CHWP-161-2
VFD CHWP-155-2 | KT | VFD | L155 | 1 | BMU/MEP Level 155 | 155-MSMDB-1 | CHWP-155-2
VFD CHWP-155-3 | KT | VFD | L155 | 2 | BMU/MEP Level 155 | 155-MSMDB-1 | CHWP-155-3
VFD CHWP-155-4 | KT | VFD | L155 | 3 | BMU/MEP Level 155 | 155-MSMDB-1 | CHWP-155-4
VFD CHWP-95-9 | KT | VFD | L95 | 1 | MEP Level 95 | 95-MSMDB-C1 | CHWP-95-9
VFD CHWP-95-10 | KT | VFD | L95 | 2 | MEP Level 95 | 95-MSMDB-C1 | CHWP-95-10
VFD CHWP-95-11 | KT | VFD | L95 | 3 | MEP Level 95 | 95-MSMDB-C1 | CHWP-95-11
VFD CHWP-95-1 | KT | VFD | L95 | 4 | MEP Level 95 | 95-MSMDB-A1 | CHWP-95-1
VFD CHWP-95-2 | KT | VFD | L95 | 5 | MEP Level 95 | 95-MSMDB-A1 | CHWP-95-2
VFD CHWP-95-3 | KT | VFD | L95 | 6 | MEP Level 95 | 95-MSMDB-A1 | CHWP-95-3
VFD CHWP-95-4 | KT | VFD | L95 | 7 | MEP Level 95 | 95-MSMDB-A1 | CHWP-95-4
VFD CHWP-95-5 | KT | VFD | L95 | 8 | MEP Level 95 | 95-MSMDB-A1 | CHWP-95-5
VFD CHWP-96-1 | KT | VFD | L96 | 1 | MEP Level 96 | 96-MSMDB-B1 | CHWP-96-1
VFD CHWP-96-2 | KT | VFD | L96 | 2 | MEP Level 96 | 96-MSMDB-B1 | CHWP-96-2
VFD CHWP-96-3 | KT | VFD | L96 | 3 | MEP Level 96 | 96-MSMDB-B1 | CHWP-96-3
VFD CHWP 121-1 | KT | VFD | L121 | 1 | MEP Level 121 | 121-MSMDB-1 | CHWP 121-1
VFD CHWP 121-2 | KT | VFD | L121 | 2 | MEP Level 121 | 121-MSMDB-1 | CHWP 121-2
VFD CHWP 121-3 | KT | VFD | L121 | 3 | MEP Level 121 | 121-MSMDB-1 | CHWP 121-3
VFD CHWP 121-5 | KT | VFD | L121 | 4 | MEP Level 121 | 121-MSMDB-1 | CHWP 121-5
VFD CHWP 68-1 | KT | VFD | L68 | 1 | MEP Level 68 | 68-MSMDB-C1 | CHWP 68-1
VFD CHWP 68-2 | KT | VFD | L68 | 2 | MEP Level 68 | 68-MSMDB-C1 | CHWP 68-2
VFD CHWP 68-3 | KT | VFD | L68 | 3 | MEP Level 68 | 68-MSMDB-C1 | CHWP 68-3
VFD CHWP-69-1 | KT | VFD | L69 | 1 | MEP Level 69 | 69-MSMDB-A1 | CHWP-69-1
VFD CHWP-69-2 | KT | VFD | L69 | 2 | MEP Level 69 | 69-MSMDB-A1 | CHWP-69-2
VFD CHWP-69-3 | KT | VFD | L69 | 3 | MEP Level 69 | 69-MSMDB-A1 | CHWP-69-3
VFD CHWP-40-1 | KT | VFD | L40 | 1 | MEP Level 40 | 40-MSMDB-C1 | CHWP-40-1
VFD CHWP-40-2 | KT | VFD | L40 | 2 | MEP Level 40 | 40-MSMDB-C1 | CHWP-40-2
VFD CHWP-40-3 | KT | VFD | L40 | 3 | MEP Level 40 | 40-MSMDB-C1 | STANDBY CHWP-40-3
VFD CHWP-40-4 | KT | VFD | L40 | 4 | MEP Level 40 | 40-MSMDB-C1 | CHWP-40-4
VFD CHWP-40-5 | KT | VFD | L40 | 5 | MEP Level 40 | 40-MSMDB-C1 | CHWP-40-5
VFD CHWP-40-6 | KT | VFD | L40 | 6 | MEP Level 40 | 40-MSMDB-C1 | STANDBY CHWP-40-6
VFD CHWP 39-1 | KT | VFD | L39 | 1 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-1
VFD CHWP 39-2 | KT | VFD | L39 | 2 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-2
VFD CHWP 39-6 | KT | VFD | L39 | 3 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-6
VFD CHWP 39-7 | KT | VFD | L39 | 4 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-7
VFD CHWP 39-11 | KT | VFD | L39 | 5 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-11
VFD CHWP 39-12 | KT | VFD | L39 | 6 | MEP Level 39 | 39-MSMDB-A1 | CHWP 39-12
VFD CHWP 39-3 | KT | VFD | L39 | 7 | MEP Level 39 | 39-MSMDB-A2 | CHWP 39-3
VFD CHWP 39-4 | KT | VFD | L39 | 8 | MEP Level 39 | 39-MSMDB-A2 | CHWP 39-4
VFD CHWP 39-5 | KT | VFD | L39 | 9 | MEP Level 39 | 39-MSMDB-A2 | CHWP 39-5
VFD CHWP 39-13 | KT | VFD | L39 | 10 | MEP Level 39 | 39-MSMDB-A2 | STANDBY CHWP 39-13
VFD CH-168-1 | KT | VFD | L168 | 1 | BMU Level 168 | 162-ESMDB-1 | CH-168-1
VFD CHWP-155-1 | KT | VFD | L155 | 4 | BMU/MEP Level 155 | 155-ESMDB-1 | CHWP-155-1
VFD CHWP-155-5 | KT | VFD | L155 | 5 | BMU/MEP Level 155 | 155-ESMDB-1 | STANDBY CHWP-155-5
CONTROLLER | KT | VFD | L95 | 9 | MEP Level 95 | 95-ESMDB-1 | 3NOS. BP-10
CONTROLLER | KT | VFD | L95 | 10 | MEP Level 95 | 95-ESMDB-1 | 3NOS. BP-9
VFD CHWP 95-6 | KT | VFD | L95 | 11 | MEP Level 95 | 95-ESMDB-1 | CHWP 95-6
VFD CHWP 95-7 | KT | VFD | L95 | 12 | MEP Level 95 | 95-ESMDB-1 | CHWP 95-7
VFD CHWP 95-8 | KT | VFD | L95 | 13 | MEP Level 95 | 95-ESMDB-1 | STANDBY CHWP 95-8
VFD AHU 95-C | KT | VFD | L95 | 14 | MEP Level 95 | 95-ESMDB-1 | AHU 95-C
VFD CHWP 96-4 | KT | VFD | L96 | 4 | MEP Level 96 | 96-ESMDB-A1 | CHWP 96-4
VFD AHU-96-C | KT | VFD | L96 | 5 | MEP Level 96 | 96-ESMDB-A1 | AHU-96-C
VFD AHU-122-C | KT | VFD | L122 | 1 | MEP Level 122 | 122-ESMDB-B2 | AHU-122-C
CONTROLLER | KT | VFD | L121 | 5 | MEP Level 121 | 121-ESMDB-1 | 4NOS. BP-11
CONTROLLER | KT | VFD | L121 | 6 | MEP Level 121 | 121-ESMDB-1 | 4NOS. BP-12
VFD AHU-146-1 | KT | VFD | L146 | 1 | Level 146 | 146-ESMDB-1 | AHU-146-1
VFD AHU-146-2 | KT | VFD | L146 | 2 | Level 146 | 146-ESMDB-1 | AHU-146-2
CONTROLLER | KT | VFD | L146 | 3 | Level 146 | 146-ESMDB-1 | 3NOS. BP-13
VFD AHU-40-1 | KT | VFD | L40 | 7 | MEP Level 40 | 40-ESMDB-B1-1 | AHU-40-1
VFD AHU-40-C | KT | VFD | L40 | 8 | MEP Level 40 | 40-ESMDB-B1-1 | AHU-40-C
VFD AHU-69-C | KT | VFD | L69 | 4 | MEP Level 69 | 69-ESMDB-B1 | AHU-69-C
VFD CHWP-69-4 | KT | VFD | L69 | 5 | MEP Level 69 | 69-ESMDB-B1 | STANDBY CHWP-69-4
VFD AHU-68-C | KT | VFD | L68 | 4 | MEP Level 68 | 68-ESMDB-B1 | AHU-68-C
CONTROLLER | KT | VFD | L68 | 5 | MEP Level 68 | 68-ESMDB-B1 | 3NOS. BP-7
CONTROLLER | KT | VFD | L68 | 6 | MEP Level 68 | 68-ESMDB-B1 | 3NOS. BP-8
VFD AHU-B3-H-1 | KT | VFD | B3 | 1 | Parking/MEP Level B3 | AHU-B3-H-1 | AHU-B3-H-1
VFD AHU-B3-H-2 | KT | VFD | B3 | 2 | Parking/MEP Level B3 | AHU-B3-H-2 | AHU-B3-H-2
VFD AHU-B1-H-1 | KT | VFD | B1 | 20 | Parking Level B1 | B2-ESMDB-T1-1 | AHU-B1-H-1
VFD AHU-B1-H-2 | KT | VFD | B1 | 21 | Parking Level B1 | B2-ESMDB-T1-1 | AHU-B1-H-2
VFD AHU-B1-1 | KT | VFD | B1 | 22 | Parking Level B1 | B2-ESMDB-T1-1 | AHU-B1-1
VFD AHU-4-H-1 | KT | VFD | L4 | 1 | Spa Level 4 | 4-ESMDB-T1-1 | AHU-4-H-1
VFD AHU-4-H-11 | KT | VFD | L4 | 2 | Spa Level 4 | 4-ESMDB-T1-1 | AHU-4-H-11
VFD AHU-4-1 | KT | VFD | L4 | 3 | Spa Level 4 | 4-ESMDB-T1-1 | AHU-4-1
VFD AHU-2-1 | KT | VFD | L2 | 1 | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | AHU-2-1
VFD AHU-2-2 | KT | VFD | L2 | 2 | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | AHU-2-2
VFD AHU-2-3 | KT | VFD | L2 | 3 | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | AHU-2-3
VFD AHU-15-1 | KT | VFD | L15 | 3 | MEP Level 15 | 15-ESMDB-A1 | AHU-15-1
VFD AHU-15-6 | KT | VFD | L15 | 4 | MEP Level 15 | 15-ESMDB-A1 | AHU-15-6
VFD AHU-15-11 | KT | VFD | L15 | 5 | MEP Level 15 | 15-ESMDB-A1 | AHU-15-11
VFD AHU-15-12 | KT | VFD | L15 | 6 | MEP Level 15 | 15-ESMDB-A1 | AHU-15-12
VFD AHU-15-5 | KT | VFD | L15 | 7 | MEP Level 15 | 15-ESMDB-B1 | AHU-15-5
VFD RF-15-5 | KT | VFD | L15 | 8 | MEP Level 15 | 15-ESMDB-B1 | RF-15-5
VFD AHU-15-4 | KT | VFD | L15 | 9 | MEP Level 15 | 15-ESMDB-B1 | AHU-15-4
VFD RF-15-4 | KT | VFD | L15 | 10 | MEP Level 15 | 15-ESMDB-B1 | RF-15-4
VFD AHU-15-2 | KT | VFD | L15 | 11 | MEP Level 15 | 15-ESMDB-B1 | AHU-15-2
VFD RF-15-13 | KT | VFD | L15 | 12 | MEP Level 15 | 15-ESMDB-B1 | RF-15-13
VFD AHU-15-3 | KT | VFD | L15 | 13 | MEP Level 15 | 15-ESMDB-C2 | AHU-15-3
VFD RF-15-3 | KT | VFD | L15 | 14 | MEP Level 15 | 15-ESMDB-C2 | RF-15-3
VFD AHU-15-7 | KT | VFD | L15 | 15 | MEP Level 15 | 15-ESMDB-C2 | AHU-15-7
CONTROLLER | KT | VFD | L15 | 16 | MEP Level 15 | 15-ESMDB-C2 | 4NOS. BP-3
CONTROLLER | KT | VFD | L15 | 17 | MEP Level 15 | 15-ESMDB-C2 | 4NOS. BP-4
VFD AHU-15-8 | KT | VFD | L15 | 18 | MEP Level 15 | 15-ESMDB-C1 | AHU-15-8
VFD RF-15-8 | KT | VFD | L15 | 19 | MEP Level 15 | 15-ESMDB-C1 | RF-15-8
VFD AHU-15-9 | KT | VFD | L15 | 20 | MEP Level 15 | 15-ESMDB-C1 | AHU-15-9
VFD RF-15-9 | KT | VFD | L15 | 21 | MEP Level 15 | 15-ESMDB-C1 | RF-15-9
VFD AHU-15-10 | KT | VFD | L15 | 22 | MEP Level 15 | 15-ESMDB-C1 | AHU-15-10
VFD RF-15-10 | KT | VFD | L15 | 23 | MEP Level 15 | 15-ESMDB-C1 | RF-15-10
VFD AHU-15-C | KT | VFD | L15 | 24 | MEP Level 15 | 15-ESMDB-C1 | AHU-15-C
VFD RF-15-C | KT | VFD | L15 | 25 | MEP Level 15 | 15-ESMDB-C1 | RF-15-C
VFD AHU-16-1 | KT | VFD | L16 | 6 | MEP Level 16 | 16-ESMDB-B1 | AHU-16-1
VFD AHU-16-2 | KT | VFD | L16 | 7 | MEP Level 16 | 16-ESMDB-B1 | AHU-16-2
VFD AHU-16-C | KT | VFD | L16 | 8 | MEP Level 16 | 16-ESMDB-B1 | AHU-16-C
VFD CHWP-16-6 | KT | VFD | L16 | 9 | MEP Level 16 | 16-ESMDB-B1 | CHWP-16-6
VFD AHU-18-1 | KT | VFD | L18 | 1 | MEP Level 18 | 18-ESMDB-1 | AHU-18-1
VFD AHU-18-2 | KT | VFD | L18 | 2 | MEP Level 18 | 18-ESMDB-1 | AHU-18-2
VFD AHU-18-3 | KT | VFD | L18 | 3 | MEP Level 18 | 18-ESMDB-1 | AHU-18-3
VFD AHU-39-C | KT | VFD | L39 | 11 | MEP Level 39 | 39-ESMDB-C1 | AHU-39-C
CONTROLLER | KT | VFD | L39 | 12 | MEP Level 39 | 39-ESMDB-C1 | 5NOS. BP-5
CONTROLLER | KT | VFD | L39 | 13 | MEP Level 39 | 39-ESMDB-C1 | 5NOS. BP-6
VFD CHWP-39-8 | KT | VFD | L39 | 14 | MEP Level 39 | 39-ESMDB-B2 | CHWP-39-8
VFD CHWP-39-9 | KT | VFD | L39 | 15 | MEP Level 39 | 39-ESMDB-B2 | CHWP-39-9
VFD CHWP-39-10 | KT | VFD | L39 | 16 | MEP Level 39 | 39-ESMDB-B2 | STANDBY CHWP-39-10
CONTROLLER | KT | VFD | B3 | 3 | Parking/MEP Level B3 | B3-ESMDB-N-1 | 5NOS. BP-1
CONTROLLER | KT | VFD | B3 | 4 | Parking/MEP Level B3 | B3-ESMDB-N-1 | 5NOS. BP-2
VFD AHU-B1-H-3 | KT | VFD | B1 | 23 | Parking Level B1 | B1-ESMDB-A1-4 | AHU-B1-H-3
VFD CHWP-B1-12 | KT | VFD | B1 | 24 | Parking Level B1 | B1-ESMDB-A1-4 | CHWP-B1-12
VFD CHWP-B1-22 | KT | VFD | B1 | 25 | Parking Level B1 | B1-ESMDB-A1-4 | CHWP-B1-22
VFD CHWP-B1-5 | KT | VFD | B1 | 26 | Parking Level B1 | B1-ESMDB-A2-5 | CHWP-B1-5
VFD CHWP-B1-6 | KT | VFD | B1 | 27 | Parking Level B1 | B1-ESMDB-A2-5 | STANDBY CHWP-B1-6
VFD CHWP-B1-11 | KT | VFD | B1 | 28 | Parking Level B1 | B1-ESMDB-A2-5 | CHWP-B1-11
VFD EGF-B1-1 | KT | VFD | B1 | 29 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-1
VFD EGF-B1-2 | KT | VFD | B1 | 30 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-2
VFD EGF-B1-3 | KT | VFD | B1 | 31 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-3
VFD EGF-B1-4 | KT | VFD | B1 | 32 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-4
VFD EGF-B1-5 | KT | VFD | B1 | 33 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-5
VFD EGF-B1-6 | KT | VFD | B1 | 34 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-6
VFD EGF-B1-7 | KT | VFD | B1 | 35 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-7
VFD EGF-B1-8 | KT | VFD | B1 | 36 | Parking Level B1 | B1-ESMDB-A1-1 | EGF-B1-8
VFD LDEF-B1-1 | KT | VFD | B1 | 37 | Parking Level B1 | B1-ESMDB-A1-1 | LDEF-B1-1
VFD EGF-B2-1 | KT | VFD | B2 | 1 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-1
VFD EGF-B2-2 | KT | VFD | B2 | 2 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-2
VFD EGF-B2-3 | KT | VFD | B2 | 3 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-3
VFD EGF-B2-4 | KT | VFD | B2 | 4 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-4
VFD EGF-B2-5 | KT | VFD | B2 | 5 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-5
VFD EGF-B2-6 | KT | VFD | B2 | 6 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-6
VFD EGF-B2-7 | KT | VFD | B2 | 7 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-7
VFD EGF-B2-8 | KT | VFD | B2 | 8 | Parking/MEP Level B2 | B2-ESMDB-B1-1 | EGF-B2-8
VFD AHU-B1-H-8 | KT | VFD | B1 | 38 | Parking Level B1 | B1-ESMDB-B1-1 | AHU-B1-H-8
VFD LDEF-B1-2 | KT | VFD | B1 | 39 | Parking Level B1 | B1-ESMDB-B1-1 | LDEF-B1-2
VFD LDSF-B1-1 | KT | VFD | B1 | 40 | Parking Level B1 | B1-ESMDB-B1-1 | LDSF-B1-1
15-ATS-B1 | KT | ATS | L15 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-1A & 15-EM-LVSG-1 | 15-ESMDB-B1
15-ATS-C | KT | ATS | L15 | 2 | Electrical Plants at Level 15/16 | 16-LVSG-1B & 15-EM-LVSG-1 | 15-EMSMDB-C1
15-ATS-B2 | KT | ATS | L15 | 3 | Electrical Plants at Level 15/16 | 16-LVSG-1B & 15-EM-LVSG-1 | 15-CSMDB-B1
15-FPC-1 | KT | ATS | L15 | 4 | Electrical Plants at Level 15/16 | 15-T-2A & 15-EM-LVSG-1 | PRIMARY FIRE PUMP TP-01
15-FPC-2 | KT | ATS | L15 | 5 | Electrical Plants at Level 15/16 | 15-T-2B & 16-EM-LVSG-1 | STANDBY FIRE PUMP TP-02
15-ATS-B3 | KT | ATS | L15 | 6 | Electrical Plants at Level 15/16 | 16-LVSG-2B & 15-EM-LVSG-1 | 15-EMSMDB-B1
16-ATS-B1 | KT | ATS | L16 | 1 | Electrical Plants at Level 15/16 | 16-LVSG-3A & 16-EM-LVSG-1 | 16-ESMDB-B1
16-ATS-2 | KT | ATS | L16 | 2 | Electrical Plants at Level 15/16 | 16-LVSG-3B & 16-EM-LVSG-1 | 16-EBVSMDB-1
B2-ATS-T1-7 | KT | ATS | B2 | 1 | Parking/MEP Level B2 | B2-LVSG-2 (SIDE-A) & B2-EM-LVSG-2 | 2M-EBVSMDB-T1-1
B2-ATS-T1-4 | KT | ATS | B2 | 2 | Parking/MEP Level B2 | B2-LVSG-2 (SIDE-A) & B2-EM-LVSG-1 | 2-ESMDB-T1-1
B2-ATS-T1-8 | KT | ATS | B2 | 3 | Parking/MEP Level B2 | B2-LVSG-2 (SIDE-B) & B2-EM-LVSG-2 | 2M-EBVSMDB-T1-2
B2-ATS-T1-5 | KT | ATS | B2 | 4 | Parking/MEP Level B2 | B2-BSMDB-T1-3 & B2-ESMDB-T1-2 | B2-ELSMDB-T1-1
B2-ATS-T1-6 | KT | ATS | B2 | 5 | Parking/MEP Level B2 | B2-BSMDB-T1-3 & B2-ESMDB-T1-2 | B2-CSMDB-T1-1
B2-ATS-T1-1 | KT | ATS | B2 | 6 | Parking/MEP Level B2 | B2-LVSG-3 (SIDE-A) & B2-EM-LVSG-1 | B3-ESMDB-C2-1
B2-ATS-T1-2 | KT | ATS | B2 | 7 | Parking/MEP Level B2 | B2-LVSG-3 (SIDE-B) & B2-EM-LVSG-1 | B2-ESMDB-T1-1
B2-ATS-T1-3 | KT | ATS | B2 | 8 | Parking/MEP Level B2 | B2-LVSG-3 (SIDE-B) & B2-EM-LVSG-1 | 4-ESMDB-T1-1
B1-ATS-N-3 | KT | ATS | B1 | 1 | Parking Level B1 | B1-LVSG-1 (SIDE-A) & B1-EM-LVSG-1 | B3-ESMDB-N-1
B1-ATS-N-4 | KT | ATS | B1 | 2 | Parking Level B1 | B1-LVSG-1 (SIDE-A) & B1-EM-LVSG-1 | B3-ESMDB-A1-1
B3-PFPC-1 | KT | ATS | B3 | 1 | Parking/MEP Level B3 | B1-T-1B & B1-EM-LVSG-1 | PRIMARY FIRE PUMP FP-01
B3-SFPC-1 | KT | ATS | B3 | 2 | Parking/MEP Level B3 | B1-T-1B & B1-EM-LVSG-1 | STANDBY FIRE PUMP FP-02
B1-ATS-N-2 | KT | ATS | B1 | 3 | Parking Level B1 | B1-LVSG-2 (SIDE-A) & B1-EM-LVSG-2 | B1-ESMDB-A1-4
B1-ATS-N-7 | KT | ATS | B1 | 4 | Parking Level B1 | B1-LVSG-2 (SIDE-A) & B1-EM-LVSG-2 | B1-ESMDB-A1-1
B1-ATS-N-8 | KT | ATS | B1 | 5 | Parking Level B1 | B1-LVSG-2 (SIDE-A) & B1-EM-LVSG-2 | B1-ESMDB-A2-5
B3-SFPC-2 | KT | ATS | B3 | 3 | Parking/MEP Level B3 | B1-T-2B & B1-EM-LVSG-2 | STANDBY FIRE PUMP HP-03
B3-SFPC-3 | KT | ATS | B3 | 4 | Parking/MEP Level B3 | B1-T-2B & B1-EM-LVSG-2 | PRIMARY FIRE PUMP HP-04
B1-ATS-N-1 | KT | ATS | B1 | 6 | Parking Level B1 | B1-LVSG-3 (SIDE-A) & B1-EM-LVSG-1 | B2-ESMDB-A1-1
B1-ATS-N-5 | KT | ATS | B1 | 7 | Parking Level B1 | B1-MSMDB-T1-6 & B1-ESMDB-N-2 | B1-CSMDB-N-1
B1-ATS-N-6 | KT | ATS | B1 | 8 | Parking Level B1 | B1-MSMDB-T1-6 & B1-ESMDB-N-2 | B1-ELSMDB-N-1
B3-PFPC-2 | KT | ATS | B3 | 5 | Parking/MEP Level B3 | B1-T-3B & B1-EM-LVSG-1 | PRIMARY FIRE PUMP HP-01
B3-PFPC-3 | KT | ATS | B3 | 6 | Parking/MEP Level B3 | B1-T-3B & B1-EM-LVSG-1 | PRIMARY FIRE PUMP HP-02
B1-ATS-S-2 | KT | ATS | B1 | 9 | Parking Level B1 | B2-LVSG-4 (SIDE-A) & B2-ESMDB-S-1 | B1-ESMDB-B1-1
B1-ATS-B1-1 | KT | ATS | B1 | 10 | Parking Level B1 | B2-LVSG-4 (SIDE-A) & B2-EM-LVSG-2 | B1-ESMDB-B1-1
B3-ATS-S-1 | KT | ATS | B3 | 7 | Parking/MEP Level B3 | B2-LVSG-4 (SIDE-B) & B2-EM-LVSG-3 | B3-ESMDB-B1-1
B3-ATS-S-2 | KT | ATS | B3 | 8 | Parking/MEP Level B3 | B2-LVSG-4 (SIDE-B) & B2-EM-LVSG-3 | B3-ESMDB-B2-1
B2-ATS-S-9 | KT | ATS | B2 | 9 | Parking/MEP Level B2 | B2-LVSG-5 (SIDE-A) & B2-EM-LVSG-3 | B2-ESMDB-B2-2
B2-ATS-S-8 | KT | ATS | B2 | 10 | Parking/MEP Level B2 | B2-MSMDB-S-4 & B2-EMSMDB-S-3 | B2-ELSMDB-S-1
B2-ATS-S-6 | KT | ATS | B2 | 11 | Parking/MEP Level B2 | B2-MSMDB-S-4 & B2-ESMDB-S-1 | B2-ESMDB-B1-1
B2-ATS-S-7 | KT | ATS | B2 | 12 | Parking/MEP Level B2 | B2-MSMDB-S-4 & B2-EMSMDB-S-3 | B2-CSMDB-S-1
140-ATS-1 | KT | ATS | L140 | 1 | Void Level 140 | 148-LVSG-1 (SIDE-A) & 140-EM-LVSG-1 | 140-ESMDB-2
162-ATS-5 | KT | ATS | L162 | 1 | MEP Level 162 | 148- LVSG-1 (SIDE-B) & 162-EBVSMDB-1 | 162-EVSMDB-1
140-ATS-3 | KT | ATS | L140 | 2 | Void Level 140 | 148-BSMDB-B1 & 140-ESMDB-1 | 140-CSMDB-1
140-ATS-2 | KT | ATS | L140 | 3 | Void Level 140 | 148-BSMDB-B1 & 140-ESMDB-1 | 140-ELSMDB-1
164-PFPC-1 | KT | ATS | L164 | 1 | Level 164 | 162-T-1A & 162-EM-LVSG-1 | PRIMARY FIRE PUMP FP-03
164-PFPC-2 | KT | ATS | L164 | 2 | Level 164 | 162-T-1A & 162-EM-LVSG-1 | PRIMARY FIRE PUMP FP-05
164-SFPC-1 | KT | ATS | L164 | 3 | Level 164 | 162-T-1B & 162-EM-LVSG-1 | STANDBY FIRE PUMP FP-04
164-SFPC-2 | KT | ATS | L164 | 4 | Level 164 | 162-T-1B & 162-EM-LVSG-1 | SECONDARY FIRE PUMP FP-06
162-ATS-1 | KT | ATS | L162 | 2 | Level 162 | 162-EMSMDB-1 & 162-EM-LVSG-1 | 162-ESMDB-1
162-ATS-2 | KT | ATS | L162 | 3 | Level 162 | 162-EMSMDB-1 & 162-ESMDB-3 | 162-ELSMDB-1
162-ATS-3 | KT | ATS | L162 | 4 | Level 162 | 162-EMSMDB-1 & 162-ESMDB-3 | 162-CSMDB-1
162-ATS-6 | KT | ATS | L162 | 5 | Level 162 | 162-MSMDB-1 & 162-EBVSMDB-1 | 171-EVSMDB-1
162-ATS-4 | KT | ATS | L162 | 6 | Level 162 | 162-LVSG-1 (SIDE-B) & 162-EM-LVSG-1 | 162-ESMDB-2
95-FPC-2 | KT | ATS | L95 | 1 | MEP Level 95 | 95-T-1A & 96-EM-LVSG-1 | STANDBY FIRE PUMP TP-08
95-FPC-1 | KT | ATS | L95 | 2 | MEP Level 95 | 95-T-1A & 96-EM-LVSG-1 | PRIMARY FIRE PUMP TP-07
95-ATS-1 | KT | ATS | L95 | 3 | MEP Level 95 | 96-LVSG-1 (SIDE-B) & 96-EM-LVSG-1 | 95-ESMDB-1
96-ATS-5 | KT | ATS | L96 | 1 | MEP Level 96 | 89-BSMDB-1 & 96-ESMDB-1 | 96-ELSMDB-1
96-ATS-4 | KT | ATS | L96 | 2 | MEP Level 96 | 89-BSMDB-1 & 96-ESMDB-1 | 96-CSMDB-1
96-ATS-2 | KT | ATS | L96 | 3 | MEP Level 96 | 96-LVSG-2A & 96-ESMDB-1 | 96-ESMDB-A1
95/96-ATS-6 | KT | ATS | L96 | 4 | MEP Level 96 | 96-LVSG-2B & 96-EM-LVSG-1 | 85-EVSMDB-1
88/89-ATS-1 | KT | ATS | L95 | 4 | MEP Level 95 | 96-LVSG-2B & 96-EM-LVSG-1 | 88/89-EVSMDB-1
121-FPC-1 | KT | ATS | L121 | 1 | MEP Level 121 | 121-T-1A & 122-EM -LVSG-1 | PRIMARY FIRE PUMP TP-09
121-FPC-2 | KT | ATS | L121 | 2 | MEP Level 121 | 121-T-1B & 122-EM -LVSG-1 | STANDBY FIRE PUMP TP-10
122-ATS-5 | KT | ATS | L122 | 1 | MEP Level 122 | 121-BSMDB-1 & 122-ESMDB-2 | 122-ELSMDB-1
122-ATS-4 | KT | ATS | L122 | 2 | MEP Level 122 | 121-BSMDB-1 & 122-ESMDB-2 | 122-CSMDB-1
121/122-ATS-3 | KT | ATS | L121 | 3 | MEP Level 121 | 121-BSMDB-1 & 122-EM-LVSG-1 | 121-EVSMDB-1
122-ATS-2 | KT | ATS | L122 | 3 | MEP Level 122 | 122-LVSG-2 (SIDE-A) & 122-ESMDB-B1 | 122-ESMDB-B2
121-ATS-1 | KT | ATS | L121 | 4 | MEP Level 121 | 122-LVSG-2 (SIDE-B) & 122-ESMDB-B1 | 121-ESMDB-1
68-FPC-1 | KT | ATS | L68 | 1 | MEP Level 68 | 68-T-2B & 69-EM-LVSG-1 | PRIMARY FIRE PUMP TP-05
68-FPC-2 | KT | ATS | L68 | 2 | MEP Level 68 | 68-T-2B & 69-EM-LVSG-1 | STANDBY FIRE PUMP TP-06
69-ATS-3 | KT | ATS | L69 | 1 | MEP Level 69 | 69-LVSG-2A & 69-EM-LVSG-1 | 69-EBVSMDB-1
69-ATS-6 | KT | ATS | L69 | 2 | MEP Level 69 | 69-LVSG-2B & 69-EM-LVSG-1 | 71-EVSMDB-3
69-ATS-5 | KT | ATS | L69 | 3 | MEP Level 69 | 69-ESMDB-B2 & 69-ESMDB-B3 | 69-ELSMDB-B1
69-ATS-4 | KT | ATS | L69 | 4 | MEP Level 69 | 69-ESMDB-B2 & 69-ESMDB-B3 | 69-CSMDB-B1
68-ATS-1 | KT | ATS | L68 | 3 | MEP Level 68 | 69-LVSG-3A & 69-EM-LVSG-1 | 68-ESMDB-B1
69-ATS-2 | KT | ATS | L69 | 5 | MEP Level 69 | 69-LVSG-3A & 69-EM-LVSG-1 | 69-ESMDB-B1
40-ATS-B1 | KT | ATS | L40 | 1 | MEP Level 40 | 40-LVSG-2A & 40-EM-LVSG-1 | 40-ESMDB-B1-1
40-ATS-4 | KT | ATS | L40 | 2 | MEP Level 40 | 40-ESMDB-B1-2 & 40-MSMDB-B2 | 40-CSMDB-B1
40-ATS-5 | KT | ATS | L40 | 3 | MEP Level 40 | 40-ESMDB-B1-2 & 40-MSMDB-B2 | 40-ELSMDB-B1
39-FPC-1 | KT | ATS | L39 | 1 | MEP Level 39 | 39-T-3A & 40-EM-LVSG-1 | PRIMARY FIRE PUMP TP-03
39-FPC-2 | KT | ATS | L39 | 2 | MEP Level 39 | 39-T-3B & 40-EM-LVSG-1 | STANDBY FIRE PUMP TP-04
39-ATS-B1 | KT | ATS | L39 | 3 | MEP Level 39 | 40-LVSG-3A & 16-EM-LVSG-1 | 39-ESMDB-B2
39-ATS-C1 | KT | ATS | L39 | 4 | MEP Level 39 | 40-LVSG-3A & 16-EM-LVSG-1 | 39-ESMDB-C1
46-ATS-1 | KT | ATS | L46 | 1 | Residential Group 1 Level 46 | 40-LVSG-3B & 40-EM-LVSG-1 | 46-EVSMDB-1
39-ATS-3 | KT | ATS | L39 | 5 | MEP Level 39 | 40-LVSG-3B & 40-EM-LVSG-1 | 39-EBVSMDB-1
13-PDB-1 | KT | DB | L10 | 1 | Office Level 10 | 13-BSMDB-1 | TBC
12-PDB-1 | KT | DB | L9 | 1 | Office Level 9 | 12-BSMDB-1 | TBC
11-PDB-1 | KT | DB | L8 | 1 | Office Level 8 | 11-BSMDB-1 | TBC
10-PDB-1 | KT | DB | L7 | 1 | Office Level 7 | 10-BSMDB-1 | TBC
9-PDB-1 | KT | DB | L13 | 1 | Office Level 13 | 9-BSMDB-1 | TBC
8-PDB-1 | KT | DB | L12 | 1 | Office Level 12 | 8-BSMDB-1 | TBC
7-PDB-1 | KT | DB | L11 | 1 | Office Level 11 | 7-BSMDB-1 | TBC
16-PDB-1 | KT | DB | L16 | 1 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | TBC
16-MDB-A1 | KT | DB | L16 | 2 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | TBC
16-MDB-A2 | KT | DB | L16 | 3 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | TBC
16-MDB-B1 | KT | DB | L16 | 4 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | TBC
16-MDB-B2 | KT | DB | L16 | 5 | Electrical Plants at Level 15/16 | 16-MSMDB-B1 | TBC
16-MDB-C1 | KT | DB | L16 | 6 | Electrical Plants at Level 15/16 | 16-MSMDB-C1 | TBC
15-MDB-A1 | KT | DB | L15 | 1 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | TBC
15-MDB-A2 | KT | DB | L15 | 2 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | TBC
15-MDB-B1 | KT | DB | L15 | 3 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | TBC
15-MDB-C1 | KT | DB | L15 | 4 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | TBC
15-PDB-1 | KT | DB | L15 | 5 | Electrical Plants at Level 15/16 | 15-MSMDB-B1 | TBC
18-PDB-1 | KT | DB | L18 | 1 | Refuge Area Level 18 | 300A CB | TBC
20-PDB-1 | KT | DB | L20 | 1 | Hotel Level 20 | 20-BSMDB-1 | TBC
21-PDB-1 | KT | DB | L21 | 1 | Hotel Level 21 | 21-BSMDB-1 | TBC
22-PDB-1 | KT | DB | L22 | 1 | Hotel Level 22 | 22-BSMDB-1 | TBC
23-PDB-1 | KT | DB | L23 | 1 | Hotel Level 23 | 23-BSMDB-1 | TBC
24-PDB-1 | KT | DB | L24 | 1 | Hotel Level 24 | 24-BSMDB-1 | TBC
25-PDB-1 | KT | DB | L25 | 1 | Hotel Level 25 | 25-BSMDB-1 | TBC
26-PDB-1 | KT | DB | L26 | 1 | Hotel Level 26 | 26-BSMDB-1 | TBC
28-PDB-1 | KT | DB | L28 | 1 | Service Apartments Level 28 | 28-BSMDB-1 | TBC
29-PDB-1 | KT | DB | L29 | 1 | Service Apartments Level 29 | 29-BSMDB-1 | TBC
30-PDB-1 | KT | DB | L30 | 1 | Service Apartments Level 30 | 30-BSMDB-1 | TBC
31-PDB-1 | KT | DB | L31 | 1 | Service Apartments Level 31 | 31-BSMDB-1 | TBC
32-PDB-1 | KT | DB | L32 | 1 | Service Apartments Level 32 | 32-BSMDB-1 | TBC
33-PDB-1 | KT | DB | L33 | 1 | Service Apartments Level 33 | 33-BSMDB-1 | TBC
34-PDB-1 | KT | DB | L34 | 1 | Service Apartments Level 34 | 34-BSMDB-1 | TBC
35-PDB-1 | KT | DB | L35 | 1 | Service Apartments Level 35 | 35-BSMDB-1 | TBC
36-PDB-1 | KT | DB | L36 | 1 | Service Apartments Level 36 | 36-BSMDB-1 | TBC
37-PDB-1 | KT | DB | L37 | 1 | Service Apartments Level 37 | 37-BSMDB-1 | TBC
38-PDB-1 | KT | DB | L38 | 1 | Service Apartments Level 38 | 38-BSMDB-1 | TBC
B1-SLDB-C1-1 | KT | DB | B2 | 1 | Parking Level B1 | B2-BSMDB-C1-1 | SITE LIGHTING
B1-SPDB-C1-1 | KT | DB | B2 | 2 | Parking Level B1 | B2-BSMDB-C1-1 | SITE POWER
B2-SLDB-C1-1 | KT | DB | B2 | 3 | Parking/MEP Level B2 | B2-BSMDB-C1-1 | SITE LIGHTING
B2-SPDB-C1-1 | KT | DB | B2 | 4 | Parking/MEP Level B2 | B2-BSMDB-C1-1 | SITE POWER
B1-LDB-C1 | KT | DB | B2 | 5 | Parking Level B1 | B2-BSMDB-C1-1 | TBC
B3-LDB-C1 | KT | DB | B2 | 6 | Parking/MEP Level B3 | B2-BSMDB-C1-1 | TBC
B1-PDB-C1-1 | KT | DB | B2 | 7 | Parking Level B1 | B2-BSMDB-C1-1 | TBC
B2-PDB-C1-1 | KT | DB | B2 | 8 | Parking/MEP Level B2 | B2-BSMDB-C1-1 | TBC
B3-PDB-C1-1 | KT | DB | B3 | 1 | Parking/MEP Level B3 | B2-BSMDB-C1-1 | TBC
B3-SLDB-C2-1 | KT | DB | B3 | 2 | Parking/MEP Level B3 | B2-BSMDB-C2-1 | SITE LIGHTING
B3-SPDB-C2-1 | KT | DB | B3 | 3 | Parking/MEP Level B3 | B2-BSMDB-C2-1 | SITE POWER
B3-LDB-C2 | KT | DB | B3 | 4 | Parking/MEP Level B3 | B2-BSMDB-C2-1 | TBC
B3-PDB-C2-1 | KT | DB | B3 | 5 | Parking/MEP Level B3 | B2-BSMDB-C2-1 | TBC
B1M-LDB-T1 | KT | DB | B1M | 1 | B1 Mezzanine | B2-BSMDB-T1-2 | TBC
B1-LDB-T1 | KT | DB | B1 | 1 | Parking Level B1 | B2-BSMDB-T1-2 | TBC
B2-LDB-T2 | KT | DB | B2 | 9 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | LOADING DOCK
B2-PDB-T2 | KT | DB | B2 | 10 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | LOADING DOCK
B2-LDB-T1-1 | KT | DB | B2 | 11 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | TBC
B1-PDB-T1-1 | KT | DB | B1 | 2 | Parking Level B1 | B2-BSMDB-T1-2 | TBC
B1-PDB-T1-2 | KT | DB | B1 | 3 | Parking Level B1 | B2-BSMDB-T1-2 | TBC
B2-PDB-T1-1 | KT | DB | B2 | 12 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | TBC
B2-PDB-T1-2 | KT | DB | B2 | 13 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | TBC
B2-PDB-T1-3 | KT | DB | B2 | 14 | Parking/MEP Level B2 | B2-BSMDB-T1-2 | TBC
B3-PDB-T1-1 | KT | DB | B3 | 6 | Parking/MEP Level B3 | B2-BSMDB-T1-2 | CATHODIC PROTECTION
B3-PDB-T3-1 | KT | DB | B3 | 7 | Parking/MEP Level B3 | B2-BSMDB-T1-2 | TBC
B1M-FPDB-T1-1 | KT | DB | B1M | 2 | B1 Mezzanine | B1M-MSMDB-T1-1 | WATER FEATURES
B1M-FPDB-T1-2 | KT | DB | B1M | 3 | B1 Mezzanine | B1M-MSMDB-T1-1 | WATER FEATURES
B1M-FPDB-T1-3 | KT | DB | B1M | 4 | B1 Mezzanine | B1M-MSMDB-T1-1 | WATER FEATURES
B1M-MDB-T1-1 | KT | DB | B1M | 5 | B1 Mezzanine | B1M-MSMDB-T1-1 | TBC
B1M-MDB-T1-2 | KT | DB | B1M | 6 | B1 Mezzanine | B1M-MSMDB-T1-1 | TBC
B1M-MDB-T1-3 | KT | DB | B1M | 7 | B1 Mezzanine | B1M-MSMDB-T1-1 | TBC
4-PDB-T1-1 | KT | DB | L4 | 1 | Spa Level 4 | 4-BSMDB-T1-1 | TBC
4-LDB-1 | KT | DB | L4 | 2 | Spa Level 4 | 4-BSMDB-T1-1 | TBC
4-MDB-T1-1 | KT | DB | L4 | 3 | Spa Level 4 | 4-BSMDB-T1-1 | TBC
4-MDB-T1-2 | KT | DB | L4 | 4 | Spa Level 4 | 4-BSMDB-T1-1 | TBC
2-PDB-T1-1 | KT | DB | L2 | 1 | Lobby/Amenities Level 2 | 2-BSMDB-T1-1 | TBC
2-LDB-1 | KT | DB | L2 | 2 | Lobby/Amenities Level 2 | 2-BSMDB-T1-1 | TBC
2-LDB-T1-2 | KT | DB | L2 | 3 | Lobby/Amenities Level 2 | 2-BSMDB-T1-1 | TBC
2-MDB-T1-1 | KT | DB | L2 | 4 | Lobby/Amenities Level 2 | 2-BSMDB-T1-1 | TBC
2-MDB-T1-2 | KT | DB | L2 | 5 | Lobby/Amenities Level 2 | 2-BSMDB-T1-1 | TBC
B1M-PDB-T1-1 | KT | DB | B1M | 8 | B1 Mezzanine | B1M-BSMDB-T1-1 | TBC
B1M-LDB-T1 | KT | DB | B1M | 9 | B1 Mezzanine | B1M-BSMDB-T1-1 | TBC
1-PDB-T1-1 | KT | DB | L1 | 1 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | TBC
1-LDB-T1-1 | KT | DB | L1 | 2 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | TBC
1-LDB-T1-2 | KT | DB | L1 | 3 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | TBC
1-MDB-T1-1 | KT | DB | L1 | 4 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | TBC
1-MDB-T1-2 | KT | DB | L1 | 5 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | TBC
B1-MDB-T1-1 | KT | DB | B1 | 4 | Parking Level B1 | B1-MSMDB-T1-1 | TBC
B1-MDB-C1-1 | KT | DB | B1 | 5 | Parking Level B1 | B1-MSMDB-T1-1 | TBC
B1-MDB-C2-1 | KT | DB | B1 | 6 | Parking Level B1 | B1-MSMDB-T1-1 | TBC
B2-MDB-C1-1 | KT | DB | B2 | 15 | Parking/MEP Level B2 | B1-MSMDB-T1-1 | TBC
B2-MDB-T1-1 | KT | DB | B2 | 16 | Parking/MEP Level B2 | B1-MSMDB-T1-1 | TBC
B2-MDB-T1-2 | KT | DB | B2 | 17 | Parking/MEP Level B2 | B1-MSMDB-T1-1 | TBC
B3-MDB-C1-1 | KT | DB | B3 | 8 | Parking/MEP Level B3 | B1-MSMDB-T1-1 | TBC
B3-MDB-C2-1 | KT | DB | B3 | 9 | Parking/MEP Level B3 | B1-MSMDB-T1-1 | TBC
B3-PDB-N-1 | KT | DB | B3 | 10 | Parking/MEP Level B3 | B1-BSMDB-N-1 | TBC
B3-LDB-N1 | KT | DB | B3 | 11 | Parking/MEP Level B3 | B1-BSMDB-N-1 | TBC
B1-LDB-N1 | KT | DB | B1 | 7 | Parking Level B1 | B1-BSMDB-N-1 | TBC
B1-PDB-N1-1 | KT | DB | B1 | 8 | Parking Level B1 | B1-BSMDB-N-1 | TBC
B1-PDB-N1-2 | KT | DB | B1 | 9 | Parking Level B1 | B1-BSMDB-N-1 | TBC
B1M-PDB-A2-1 | KT | DB | B1M | 10 | B1 Mezzanine | B1-BSMDB-A2-1 | TBC
B1-PDB-A2-1 | KT | DB | B1 | 10 | Parking Level B1 | B1-BSMDB-A2-1 | TBC
B1-LDB-A2 | KT | DB | B1 | 11 | Parking Level B1 | B1-BSMDB-A2-1 | TBC
B2-PDB-A2-1 | KT | DB | B2 | 18 | Parking/MEP Level B2 | B1-BSMDB-A2-1 | TBC
B3-PDB-A2-1 | KT | DB | B3 | 12 | Parking/MEP Level B3 | B1-BSMDB-A2-1 | TBC
B3-LDB-A2 | KT | DB | B3 | 13 | Parking/MEP Level B3 | B1-BSMDB-A2-1 | TBC
B1M-SPDB-A2-1 | KT | DB | B1M | 11 | B1 Mezzanine | B1-BSMDB-N-3 | TBC
B1-SPDB-N-1 | KT | DB | B1 | 12 | Parking Level B1 | B1-BSMDB-N-3 | TBC
B1-SLDB-N-1 | KT | DB | B1 | 13 | Parking Level B1 | B1-BSMDB-N-3 | TBC
B1M-SLDB-A2-1 | KT | DB | B1M | 12 | B1 Mezzanine | B1-BSMDB-N-3 | TBC
B3-PDB-A1-1 | KT | DB | B3 | 14 | Parking/MEP Level B3 | B1-BSMDB-A1-1 | TBC
B3-LDB-A1-1 | KT | DB | B3 | 15 | Parking/MEP Level B3 | B1-BSMDB-A1-1 | TBC
B1-MDB-A1-1 | KT | DB | B1 | 14 | Parking Level B1 | B1-MSMDB-A1-1 | TBC
B1-MDB-A1-2 | KT | DB | B1 | 15 | Parking Level B1 | B1-MSMDB-A1-1 | TBC
B2-MDB-A2-1 | KT | DB | B2 | 19 | Parking/MEP Level B2 | B1-MSMDB-A1-1 | TBC
B3-MDB-A1-1 | KT | DB | B3 | 16 | Parking/MEP Level B3 | B1-MSMDB-A1-1 | TBC
B3-MDB-A2-1 | KT | DB | B3 | 17 | Parking/MEP Level B3 | B1-MSMDB-A1-1 | TBC
B1-PDB-B1-1 | KT | DB | B2 | 20 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B1-LDB-B1 | KT | DB | B2 | 21 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B2-PDB-B1-1 | KT | DB | B2 | 22 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B2-PDB-B1-2 | KT | DB | B2 | 23 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B2-LDB-T2 | KT | DB | B2 | 24 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | LOADING DOCK
B2-PDB-T2 | KT | DB | B2 | 25 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | LOADING DOCK
B3-PDB-B1-1 | KT | DB | B2 | 26 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B3-LDB-B1 | KT | DB | B2 | 27 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B1M-PDB-B1-1 | KT | DB | B2 | 28 | Parking/MEP Level B2 | B2-BSMDB-B1-1 | TBC
B1-MDB-B1-1 | KT | DB | B2 | 29 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B1-MDB-B2-1 | KT | DB | B2 | 30 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B2-MDB-B1-1 | KT | DB | B2 | 31 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B2-MDB-B2-1 | KT | DB | B2 | 32 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B3-MDB-B1-1 | KT | DB | B2 | 33 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B3-MDB-B2-1 | KT | DB | B2 | 34 | Parking/MEP Level B2 | B2-MSMDB-B1-1 | TBC
B1M-SPDB-B1-1 | KT | DB | B2 | 35 | Parking/MEP Level B2 | B2-BSMDB-S-1 | SITE POWER
B1M-SLDB-B1-1 | KT | DB | B2 | 36 | Parking/MEP Level B2 | B2-BSMDB-S-1 | SITE LIGHTING
B1-LDB-B2 | KT | DB | B2 | 37 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B1-PDB-B2-1 | KT | DB | B2 | 38 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B2-PDB-B2-1 | KT | DB | B2 | 39 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B2-SPDB-S-1 | KT | DB | B2 | 40 | Parking/MEP Level B2 | B2-BSMDB-S-1 | SITE POWER
B2-SLDB-S-1 | KT | DB | B2 | 41 | Parking/MEP Level B2 | B2-BSMDB-S-1 | SITE LIGHTING
B3-PDB-B2-1 | KT | DB | B2 | 42 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B3-LDB-B2 | KT | DB | B2 | 43 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B2-LDB-S | KT | DB | B2 | 44 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
B3-PDB-S-1 | KT | DB | B2 | 45 | Parking/MEP Level B2 | B2-BSMDB-S-1 | TBC
146-MDB-1 | KT | DB | L146 | 1 | Level 146 | 148-MSMDB-1 | L 146
146-MDB-2 | KT | DB | L146 | 2 | Level 146 | 148-MSMDB-1 | L 146
144-MDB-1 | KT | DB | L144 | 1 | Void Level 144 | 148-MSMDB-1 | L136 - L 144
134-MDB-1 | KT | DB | L134 | 1 | Void Level 134 | 148-MSMDB-1 | L 130 - L 134
132-PDB-1 | KT | DB | L132 | 1 | Void Level 132 | 148-BSMDB-B1 | L 126 - L 132
140-PDB-1 | KT | DB | L140 | 1 | Void Level 140 | 148-BSMDB-B1 | L 134 - L 140
146-PDB-1 | KT | DB | L146 | 3 | Level 146 | 148-BSMDB-B1 | L 142 - L 146
148-PDB-1 | KT | DB | L148 | 1 | Void Level 148 | 162-BSMDB-1 | L 148 - L 150
152-PDB-1 | KT | DB | L152 | 1 | Void Level 152 | 162-BSMDB-1 | L 152 - L 155
157-PDB-1 | KT | DB | L157 | 1 | Level 157 | 162-BSMDB-1 | L 157 - L 159
162-PDB-1 | KT | DB | L162 | 1 | MEP Level 162 | 162-BSMDB-1 | L 161 - L 164
168-PDB-1 | KT | DB | L168 | 1 | BMU Level 168 | 162-BSMDB-1 | L 165 - L 179
184-PDB-1 | KT | DB | L184 | 1 | Slab for TMD Reserve Support | 162-BSMDB-1 | L 180 - L 200
203-PDB-1 | KT | DB | L203 | 1 | Spire Level 203 | 162-BSMDB-1 | L 201 - L 220
222-PDB-1 | KT | DB | L222 | 1 | Spire Level 222 | 162-BSMDB-1 | L 221 - L 251
161-MDB-1 | KT | DB | L161 | 1 | MEP Level 161 | 162-MSMDB-3 | L 157 - L 161
162-MDB-1 | KT | DB | L162 | 2 | MEP Level 162 | 162-MSMDB-3 | L 162
164-MDB-1 | KT | DB | L164 | 1 | Level 164 | 162-MSMDB-3 | L 164
165-MDB-1 | KT | DB | L165 | 1 | Level 165 | 162-MSMDB-3 | L 165
169-MDB-1 | KT | DB | L169 | 1 | Level 169 | 162-MSMDB-3 | L 167 - L 171
155-MDB-1 | KT | DB | L155 | 1 | BMU/MEP Level 155 | 155-MSMDB-1 | L 155
99-PDB-1 | KT | DB | L99 | 1 | Residential Group 4 Level 99 | 99-BSMDB-1 | TBC
100-PDB-1 | KT | DB | L100 | 1 | Residential Group 4 Level 100 | 100-BSMDB-1 | TBC
101-PDB-1 | KT | DB | L101 | 1 | Residential Group 4 Level 101 | 101-BSMDB-1 | TBC
102-PDB-1 | KT | DB | L102 | 1 | Residential Group 4 Level 102 | 102-BSMDB-1 | TBC
103-PDB-1 | KT | DB | L103 | 1 | Residential Group 4 Level 103 | 103-BSMDB-1 | TBC
104-PDB-1 | KT | DB | L104 | 1 | Residential Group 4 Level 104 | 200A CB | TBC
94-PDB-1 | KT | DB | L94 | 1 | Residential Group 3 Level 94 | 94-BSMDB-1 | 100A 400Y/230V PANEL
93-PDB-1 | KT | DB | L93 | 1 | Residential Group 3 Level 93 | 93-BSMDB-1 | 100A 400Y/230V PANEL
92-PDB-1 | KT | DB | L92 | 1 | Residential Group 3 Level 92 | 92-BSMDB-1 | 100A 400Y/230V PANEL
91-PDB-1 | KT | DB | L91 | 1 | Residential Group 3 Level 91 | 91-BSMDB-1 | 100A 400Y/230V PANEL
90-PDB-1 | KT | DB | L90 | 1 | Residential Group 3 Level 90 | 90-BSMDB-1 | 100A 400Y/230V PANEL
89-PDB-1 | KT | DB | L89 | 1 | Residential Group 3 Level 89 | 89-BSMDB-1 | 100A 400Y/230V PANEL
88-PDB-1 | KT | DB | L88 | 1 | Residential Group 3 Level 88 | 88-BSMDB-1 | 100A 400Y/230V PANEL
87-PDB-1 | KT | DB | L87 | 1 | Residential Group 3 Level 87 | 87-BSMDB-1 | 100A 400Y/230V PANEL
86-PDB-1 | KT | DB | L86 | 1 | Refuge Area Level 86 | 300A CB | 100A 400Y/230V PANEL
95-MDB-C1 | KT | DB | L95 | 1 | MEP Level 95 | 95-MSMDB-C1 | TBC
95-MDB-C2 | KT | DB | L95 | 2 | MEP Level 95 | 95-MSMDB-C1 | TBC
95-MDB-A1 | KT | DB | L95 | 3 | MEP Level 95 | 95-MSMDB-A1 | TBC
95-MDB-A2 | KT | DB | L95 | 4 | MEP Level 95 | 95-MSMDB-A1 | TBC
95-PDB-1 | KT | DB | L95 | 5 | MEP Level 95 | 95-MSMDB-A1 | TBC
96-MDB-A1 | KT | DB | L96 | 1 | MEP Level 96 | 96-MSMDB-B1 | TBC
96-MDB-B1 | KT | DB | L96 | 2 | MEP Level 96 | 96-MSMDB-B1 | TBC
96-MDB-C1 | KT | DB | L96 | 3 | MEP Level 96 | 96-MSMDB-B1 | TBC
96-MDB-C2 | KT | DB | L96 | 4 | MEP Level 96 | 96-MSMDB-B1 | TBC
120-PDB-1 | KT | DB | L120 | 1 | Residential Group 4 Level 120 | 120-BSMDB-1 | TBC
119-PDB-1 | KT | DB | L119 | 1 | Residential Group 4 Level 119 | 119-BSMDB-1 | TBC
118-PDB-1 | KT | DB | L118 | 1 | Residential Group 4 Level 118 | 118-BSMDB-1 | TBC
117-PDB-1 | KT | DB | L117 | 1 | Residential Group 4 Level 117 | 117-BSMDB-1 | TBC
116-PDB-1 | KT | DB | L116 | 1 | Residential Group 4 Level 116 | 116-BSMDB-1 | TBC
115-PDB-1 | KT | DB | L115 | 1 | Residential Group 4 Level 115 | 115-BSMDB-1 | TBC
114-PDB-1 | KT | DB | L114 | 1 | Residential Group 4 Level 114 | 114-BSMDB-1 | TBC
113-PDB-1 | KT | DB | L113 | 1 | Residential Group 4 Level 113 | 113-BSMDB-1 | TBC
112-PDB-1 | KT | DB | L112 | 1 | Residential Group 4 Level 112 | 112-BSMDB-1 | TBC
111-PDB-1 | KT | DB | L111 | 1 | Residential Group 4 Level 111 | 111-BSMDB-1 | TBC
110-PDB-1 | KT | DB | L110 | 1 | Residential Group 4 Level 110 | 110-BSMDB-1 | TBC
109-PDB-1 | KT | DB | L109 | 1 | Residential Group 4 Level 109 | 109-BSMDB-1 | TBC
108-PDB-1 | KT | DB | L108 | 1 | Residential Group 4 Level 108 | 108-BSMDB-1 | TBC
107-PDB-1 | KT | DB | L107 | 1 | Residential Group 4 Level 107 | 107-BSMDB-1 | TBC
106-PDB-1 | KT | DB | L106 | 1 | Residential Group 4 Level 106 | 106-BSMDB-1 | TBC
124-PDB-1 | KT | DB | L124 | 1 | Refuge Area Level 124 | 122-MSMDB-1 | REFUGE FLOOR
122-MDB-1 | KT | DB | L122 | 1 | MEP Level 122 | 122-MSMDB-1 | TBC
122-MDB-2 | KT | DB | L122 | 2 | MEP Level 122 | 122-MSMDB-1 | TBC
121-MDB-C1 | KT | DB | L121 | 1 | MEP Level 121 | 121-MSMDB-C | TBC
121-MDB-A1 | KT | DB | L121 | 2 | MEP Level 121 | 121-MSMDB-1 | TBC
121-MDB-B1 | KT | DB | L121 | 3 | MEP Level 121 | 121-MSMDB-1 | TBC
67-PDB-1 | KT | DB | L67 | 1 | Residential Group 4 Level 67 | 67-BSMDB-1 | TBC
66-PDB-1 | KT | DB | L66 | 1 | Residential Group 4 Level 66 | 66-BSMDB-1 | TBC
65-PDB-1 | KT | DB | L65 | 1 | Residential Group 4 Level 65 | 65-BSMDB-1 | TBC
64-PDB-1 | KT | DB | L64 | 1 | Residential Group 4 Level 64 | 64-BSMDB-1 | TBC
63-PDB-1 | KT | DB | L63 | 1 | Residential Group 4 Level 63 | 63-BSMDB-1 | TBC
62-PDB-1 | KT | DB | L62 | 1 | Residential Group 4 Level 62 | 62-BSMDB-1 | TBC
61-PDB-1 | KT | DB | L61 | 1 | Residential Group 4 Level 61 | 61-BSMDB-1 | TBC
60-PDB-1 | KT | DB | L60 | 1 | Residential Group 4 Level 60 | 60-BSMDB-1 | TBC
59-PDB-1 | KT | DB | L59 | 1 | Residential Group 4 Level 59 | 59-BSMDB-1 | TBC
58-PDB-1 | KT | DB | L58 | 1 | Residential Group 4 Level 58 | 58-BSMDB-1 | TBC
68-MDB-C1 | KT | DB | L68 | 1 | MEP Level 68 | 68-MSMDB-C1 | TBC
68-MDB-C2 | KT | DB | L68 | 2 | MEP Level 68 | 68-MSMDB-C1 | TBC
68-MDB-A1 | KT | DB | L68 | 3 | MEP Level 68 | 68-MSMDB-B2 | TBC
68-MDB-A2 | KT | DB | L68 | 4 | MEP Level 68 | 68-MSMDB-B2 | TBC
68-MDB-B1 | KT | DB | L68 | 5 | MEP Level 68 | 68-MSMDB-B2 | TBC
68-MDB-B2 | KT | DB | L68 | 6 | MEP Level 68 | 68-MSMDB-B2 | TBC
69-MDB-B1 | KT | DB | L69 | 1 | MEP Level 69 | 69-MSMDB-B1 | TBC
69-MDB-B2 | KT | DB | L69 | 2 | MEP Level 69 | 69-MSMDB-B1 | TBC
69-MDB-C1 | KT | DB | L69 | 3 | MEP Level 69 | 69-MSMDB-B1 | TBC
69-MDB-A1 | KT | DB | L69 | 4 | MEP Level 69 | 69-MSMDB-A1 | TBC
69-MDB-A2 | KT | DB | L69 | 5 | MEP Level 69 | 69-MSMDB-A1 | TBC
71-PDB-1 | KT | DB | L71 | 1 | Refuge Area Level 71 | 200A CB | 100A 400Y/230V PANEL
73-PDB-1 | KT | DB | L73 | 1 | Resudential Group 2 Level 73 | 73-BSMDB-1 | 100A 400Y/230V PANEL
74-PDB-1 | KT | DB | L74 | 1 | Resudential Group 2 Level 74 | 74-BSMDB-1 | 100A 400Y/230V PANEL
75-PDB-1 | KT | DB | L75 | 1 | Resudential Group 2 Level 75 | 75-BSMDB-1 | 100A 400Y/230V PANEL
76-PDB-1 | KT | DB | L76 | 1 | Resudential Group 2 Level 76 | 76-BSMDB-1 | 100A 400Y/230V PANEL
77-PDB-1 | KT | DB | L77 | 1 | Resudential Group 2 Level 77 | 77-BSMDB-1 | 100A 400Y/230V PANEL
78-PDB-1 | KT | DB | L78 | 1 | Resudential Group 2 Level 78 | 78-BSMDB-1 | 100A 400Y/230V PANEL
79-PDB-1 | KT | DB | L79 | 1 | Resudential Group 2 Level 79 | 79-BSMDB-1 | 100A 400Y/230V PANEL
80-PDB-1 | KT | DB | L80 | 1 | Resudential Group 2 Level 80 | 80-BSMDB-1 | 100A 400Y/230V PANEL
81-PDB-1 | KT | DB | L81 | 1 | Resudential Group 2 Level 81 | 81-BSMDB-1 | 100A 400Y/230V PANEL
82-PDB-1 | KT | DB | L82 | 1 | Resudential Group 2 Level 82 | 82-BSMDB-1 | 100A 400Y/230V PANEL
83-PDB-1 | KT | DB | L83 | 1 | Resudential Group 2 Level 83 | 83-BSMDB-1 | 100A 400Y/230V PANEL
84-PDB-1 | KT | DB | L84 | 1 | Sky Lobby Level 84 | 84-BSMDB-1 | TBC
84-PDB-2 | KT | DB | L84 | 2 | Sky Lobby Level 84 | 84-BSMDB-1 | TBC
84-PDB-3 | KT | DB | L84 | 3 | Sky Lobby Level 84 | 84-BSMDB-1 | TBC
84-PDB-4 | KT | DB | L84 | 4 | Sky Lobby Level 84 | 84-BSMDB-1 | TBC
40-MDB-A1 | KT | DB | L40 | 1 | MEP Level 40 | 40-MSMDB-B1 | TBC
40-MDB-A2 | KT | DB | L40 | 2 | MEP Level 40 | 40-MSMDB-B1 | TBC
40-MDB-B1 | KT | DB | L40 | 3 | MEP Level 40 | 40-MSMDB-B1 | TBC
40-MDB-B2 | KT | DB | L40 | 4 | MEP Level 40 | 40-MSMDB-B1 | TBC
40-PDB-1 | KT | DB | L40 | 5 | MEP Level 40 | 40-MSMDB-B1 | TBC
40-MDB-C1 | KT | DB | L40 | 6 | MEP Level 40 | 40-MSMDB-C1 | TBC
40-MDB-C2 | KT | DB | L40 | 7 | MEP Level 40 | 40-MSMDB-C1 | TBC
42-PDB-1 | KT | DB | L42 | 1 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
42-PDB-2 | KT | DB | L42 | 2 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
42-PDB-3 | KT | DB | L42 | 3 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
42-PDB-4 | KT | DB | L42 | 4 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
42-PDB-5 | KT | DB | L42 | 5 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
42-PDB-6 | KT | DB | L42 | 6 | Sky Lobby Level 42 | 42-BSMDB-1 | TBC
43-PDB-1 | KT | DB | L43 | 1 | Sky Lobby Level 43 | 43-BSMDB-1 | TBC
43-PDB-2 | KT | DB | L43 | 2 | Sky Lobby Level 43 | 43-BSMDB-2 | TBC
43-PDB-3 | KT | DB | L43 | 3 | Sky Lobby Level 43 | 43-BSMDB-3 | TBC
44-PDB-1 | KT | DB | L44 | 1 | Residential Group 1 Level 44 | 44-BSMDB-1 | TBC
45-PDB-1 | KT | DB | L45 | 1 | Residential Group 1 Level 45 | 45-BSMDB-1 | TBC
46-PDB-1 | KT | DB | L46 | 1 | Residential Group 1 Level 46 | 46-BSMDB-1 | TBC
47-PDB-1 | KT | DB | L47 | 1 | Residential Group 1 Level 47 | 47-BSMDB-1 | TBC
48-PDB-1 | KT | DB | L48 | 1 | Residential Group 1 Level 48 | 48-BSMDB-1 | TBC
49-PDB-1 | KT | DB | L49 | 1 | Residential Group 1 Level 49 | 49-BSMDB-1 | TBC
50-PDB-1 | KT | DB | L50 | 1 | Residential Group 1 Level 50 | 50-BSMDB-1 | TBC
51-PDB-1 | KT | DB | L51 | 1 | Residential Group 1 Level 51 | 51-BSMDB-1 | TBC
52-PDB-1 | KT | DB | L52 | 1 | Residential Group 1 Level 52 | 52-BSMDB-1 | TBC
53-PDB-1 | KT | DB | L53 | 1 | Residential Group 1 Level 53 | 53-BSMDB-1 | TBC
54-PDB-1 | KT | DB | L54 | 1 | Residential Group 1 Level 54 | 54-BSMDB-1 | TBC
55-PDB-1 | KT | DB | L55 | 1 | Residential Group 1 Level 55 | 55-BSMDB-1 | TBC
56-PDB-1 | KT | DB | L56 | 1 | Residential Group 1 Level 56 | 250A CB | TBC
39-MDB-A1 | KT | DB | L39 | 1 | MEP Level 39 | 39-MSMDB-A1 | TBC
39-MDB-A2 | KT | DB | L39 | 2 | MEP Level 39 | 39-MSMDB-A2 | TBC
39-MDB-C1 | KT | DB | L39 | 3 | MEP Level 39 | 39-MSMDB-C1 | TBC
39-MDB-C2 | KT | DB | L39 | 4 | MEP Level 39 | 39-MSMDB-C1 | TBC
39-MDB-B1 | KT | DB | L39 | 5 | MEP Level 39 | 39-MSMDB-B1 | TBC
39-MDB-B2 | KT | DB | L39 | 6 | MEP Level 39 | 39-MSMDB-B1 | TBC
39-PDB-1 | KT | DB | L39 | 7 | MEP Level 39 | 39-MSMDB-B1 | TBC
154-CDB-1 | KT | DB | L154 | 1 | Refuge Level 154 | 162-CSMDB-1 | L 154 AOR
162-CDB-1 | KT | DB | L162 | 3 | MEP Level 162 | 162-CSMDB-1 | L 155 - L 166
168-CDB-1 | KT | DB | L168 | 2 | BMU Level 168 | 162-CSMDB-1 | L 167 - L 179
184-CDB-1 | KT | DB | L184 | 2 | Slab for TMD Reserve Support | 162-CSMDB-1 | L 180 - L 200
203-CDB-1 | KT | DB | L203 | 2 | Spire Level 203 | 162-CSMDB-1 | L 201 - L 220
222-CDB-1 | KT | DB | L222 | 2 | Spire Level 222 | 162-CSMDB-1 | L 221 - L 251
154-ELDB-1 | KT | DB | L154 | 2 | Refuge Level 154 | 162-ELSMDB-1 | L 154 AOR
158-ELDB-1 | KT | DB | L158 | 1 | Level 158 | 162-ELSMDB-1 | L 155 - L 160
162-ELDB-1 | KT | DB | L162 | 4 | MEP Level 162 | 162-ELSMDB-1 | L 161 - L 166
168-ELDB-1 | KT | DB | L168 | 3 | BMU Level 168 | 162-ELSMDB-1 | L 167 - L 179
184-ELDB-1 | KT | DB | L184 | 3 | Slab for TMD Reserve Support | 162-ELSMDB-1 | L 180 - L 200
203-ELDB-1 | KT | DB | L203 | 3 | Spire Level 203 | 162-ELSMDB-1 | L 201 - L 220
222-ELDB-1 | KT | DB | L222 | 3 | Spire Level 222 | 162-ELSMDB-1 | L 221 - L 251
162-EMSB-1 | KT | DB | L162 | 5 | MEP Level 162 | 162-ESMDB-1 | SERVING L 162
161-EMDB-1 | KT | DB | L162 | 6 | MEP Level 162 | 162-ESMDB-1 | SERVING L 161
161-EMDB-2 | KT | DB | L162 | 7 | MEP Level 162 | 162-ESMDB-1 | SERVING L 161
159-EMDB-1 | KT | DB | L162 | 8 | MEP Level 162 | 162-ESMDB-1 | SERVING L 157 - L 159
164-EMDB-1 | KT | DB | L164 | 2 | Level 164 | 162-ESMDB-2 | SERVING L 163 - L 164
165-EMDB-1 | KT | DB | L165 | 2 | Level 165 | 162-ESMDB-2 | SERVING L 165 - L 166
169-EMDB-1 | KT | DB | L169 | 2 | Level 169 | 162-ESMDB-2 | SERVING L 167 - L 179
184-EMDB-1 | KT | DB | L184 | 4 | Slab for TMD Reserve Support | 162-ESMDB-2 | SERVING L 180 - L 200
203-EMDB-1 | KT | DB | L203 | 4 | Spire Level 203 | 162-ESMDB-2 | SERVING L 201 - L 220
222-EMDB-1 | KT | DB | L222 | 4 | Spire Level 222 | 162-ESMDB-2 | SERVING L 221 - L 251
155-EMDB-1 | KT | DB | L155 | 2 | BMU/MEP Level 155 | 155-ESMDB-1 | SERVING L 155
154-EMDB-1 | KT | DB | L154 | 3 | Refuge Level 154 | 155-ESMDB-1 | SERVING L 154 AOR
162-EVDB-1 | KT | DB | L162 | 9 | MEP Level 162 | 162-EVSMDB-1 | TBC
161-EVDB-1 | KT | DB | L161 | 2 | MEP Level 161 | 162-EVSMDB-1 | TBC
171-EVDB-1 | KT | DB | L171 | 1 | TMD Reserve Level 171 | 171-EVSMDB-1 | TBC
171-EVDB-2 | KT | DB | L171 | 2 | TMD Reserve Level 171 | 171-EVSMDB-1 | TBC
170-EVDB-1 | KT | DB | L170 | 1 | Spire MEP Level 170 | 171-EVSMDB-1 | TBC
88/89-EVDB-1 | KT | DB | L88 | 2 | Residential Group 3A Level 88 | 88/89-EVSMDB-1 | LIFTS
95-EMDB-1 | KT | DB | L95 | 6 | MEP Level 95 | 95-ESMDB-1 | TBC
95-EMDB-2 | KT | DB | L95 | 7 | MEP Level 95 | 95-ESMDB-1 | TBC
86-EMDB-1 | KT | DB | L86 | 2 | Refuge Area Level 86 | 95-ESMDB-1 | SERVING L86 AOR
84-EMDB-1 | KT | DB | L84 | 5 | Sky Lobby Level 84 | 95-ESMDB-1 | SERVING L 84 SKY LOBBY
96-EMDB-A1 | KT | DB | L96 | 5 | MEP Level 96 | 96-ESMDB-A1 | TBC
96-EMDB-C1 | KT | DB | L96 | 6 | MEP Level 96 | 96-ESMDB-A1 | TBC
104-EMDB-1 | KT | DB | L104 | 2 | Refuge Area Level 104 | 96-ESMDB-A1 | LIFTS SERVING AOR
86-CDB-1 | KT | DB | L86 | 3 | Refuge Area Level 86 | 96CSMDB-1 | SERVING L 86 AOR
87-CDB-1 | KT | DB | L87 | 2 | Residential Group 3A Level 87 | 96CSMDB-1 | SERVING L 87 - L 89
93-CDB-1 | KT | DB | L93 | 2 | Residential Group 3A Level 93 | 96CSMDB-1 | SERVING L 90 - L 93
96-CDB-1 | KT | DB | L96 | 7 | MEP Level 96 | 96CSMDB-1 | SERVING L 94 - L 99
102-CDB-1 | KT | DB | L102 | 2 | Residential Group 4 Level 102 | 96CSMDB-1 | SERVING L 100 - L 103
104-CDB-1 | KT | DB | L104 | 3 | Residential Group 4 Level 104 | 96CSMDB-1 | SERVING L 104 AOR
86-ELDB-1 | KT | DB | L86 | 4 | Refuge Area Level 86 | 96-ELSMDB-2 | SERVING L 86 AOR
89-ELDB-1 | KT | DB | L89 | 2 | Residential Group 3 Level 89 | 96-ELSMDB-2 | SERVING L 87 - L 91
94-ELDB-1 | KT | DB | L94 | 2 | Residential Group 3 Level 94 | 96-ELSMDB-2 | SERVING L 92 - L 96
100-ELDB-1 | KT | DB | L100 | 2 | Residential Group 4 Level 100 | 96-ELSMDB-2 | SERVING L 97 - L 103
104-ELDB-1 | KT | DB | L104 | 4 | Refuge Area Level 104 | 96-ELSMDB-2 | SERVING L 104 AOR
85-EVDB-1 | KT | DB | L85 | 1 | Sky Lobby Level 85 | 95/96-ATS-6 | LIFTS
121-EVDB-1 | KT | DB | L121 | 4 | MEP Level 121 | 121-EV-SMDB-1 | LIFTS
122-EMDB-A1 | KT | DB | L122 | 3 | MEP Level 122 | 122-ESMDB-B2 | TBC
122-EMDB-B1 | KT | DB | L122 | 4 | MEP Level 122 | 122-ESMDB-B2 | TBC
124-EMDB-1 | KT | DB | L124 | 2 | Refuge Area Level 124 | 122-ESMDB-B2 | LIFTS SERVING AOR
121-EMDB-A1 | KT | DB | L121 | 5 | MEP Level 121 | 121-ESMDB-1 | TBC
121-EMDB-C1 | KT | DB | L121 | 6 | MEP Level 121 | 121-ESMDB-1 | TBC
108-ELDB-1 | KT | DB | L108 | 2 | Residential Group 4 Level 108 | 122-ELSMDB-2 | SERVING L 106 - L 111
116-ELDB-1 | KT | DB | L116 | 2 | Residential Group 4 Level 116 | 122-ELSMDB-2 | SERVING L 112 - L 117
120-ELDB-1 | KT | DB | L120 | 2 | Residential Group 4 Level 120 | 122-ELSMDB-2 | SERVING L 118 - L 122
124-ELDB-1 | KT | DB | L124 | 3 | Refuge Area Level 124 | 122-ELSMDB-2 | SERVING L 124 AOR
106-CDB-1 | KT | DB | L106 | 2 | Residential Group 4 Level 106 | 122-CSMDB-1 | SERVING L 106 - L 109
110-CDB-1 | KT | DB | L110 | 2 | Residential Group 4 Level 110 | 122-CSMDB-1 | SERVING L 110 - L 113
114-CDB-1 | KT | DB | L114 | 2 | Residential Group 4 Level 114 | 122-CSMDB-1 | SERVING L 114 - L 117
118-CDB-1 | KT | DB | L118 | 2 | Residential Group 4 Level 118 | 122-CSMDB-1 | SERVING L 118 - L 122
124-CDB-1 | KT | DB | L124 | 4 | Refuge Area Level 124 | 122-CSMDB-1 | SERVING L 124 AOR
132-CDB-1 | KT | DB | L132 | 2 | Void Level 132 | 140-CSMDB-1 | SERVING L 126 - L 133
140-CDB-1 | KT | DB | L140 | 2 | Void Level 140 | 140-CSMDB-1 | SERVING L 134 - L 141
148-CDB-1 | KT | DB | L148 | 2 | Void Level 148 | 140-CSMDB-1 | SERVING L 142 - L 152
132-ELDB-1 | KT | DB | L132 | 3 | Void Level 132 | 140-ELSMDB-1 | SERVING L 126 - L 133
140-ELDB-1 | KT | DB | L140 | 3 | Void Level 140 | 140-ELSMDB-1 | SERVING L 134 - L 141
148-ELDB-1 | KT | DB | L148 | 3 | Void Level 148 | 140-ELSMDB-1 | SERVING L 142 - L 152
140-EMDB-1 | KT | DB | L140 | 4 | Void Level 140 | 140-ESMDB-2 | SERVING L 130 - L 140
144-EMDB-1 | KT | DB | L144 | 2 | Void Level 144 | 140-ESMDB-2 | SERVING L 142 - L 144
146-EMDB-1 | KT | DB | L146 | 4 | Void Level 146 | 146-ESMDB-1 | SERVING L 146
146-EMDB-2 | KT | DB | L146 | 5 | Void Level 146 | 146-ESMDB-1 | SERVING L 146 - L 152
28/29-EVDB-1 | KT | DB | L28 | 2 | Service Apartments Level 28 | 28/29-EVSMDB-1 | LIFTS
39-EVDB-1 | KT | DB | L39 | 8 | MEP Level 39 | 39-EVSMDB-1 | LIFTS
39-EVDB-2 | KT | DB | L39 | 9 | MEP Level 39 | 39-EVSMDB-2 | LIFTS
40-EMDB-A1 | KT | DB | L40 | 8 | MEP Level 40 | 40-ESMDB-B1-1 | TBC
40-EMDB-B1 | KT | DB | L40 | 9 | MEP Level 40 | 40-ESMDB-B1-1 | TBC
40-EMDB-C1 | KT | DB | L40 | 10 | MEP Level 40 | 40-ESMDB-B1-1 | TBC
56-EMDB-1 | KT | DB | L56 | 2 | Refuge Area Level 56 | 40-ESMDB-B1-1 | TBC
58-EMDB-1 | KT | DB | L58 | 2 | Residential Group 1 Level 58 | 40-ESMDB-B1-1 | TBC
46-EVDB-1 | KT | DB | L46 | 2 | Residential Group 1 Level 46 | 46-EVSMDB-1 | LIFTS
30-CDB-1 | KT | DB | L30 | 2 | Service Apartments Level 30 | 40-CSMDB-B1 | SERVING L 27 - L 31
34-CDB-1 | KT | DB | L34 | 2 | Service Apartments Level 30 | 40-CSMDB-B1 | SERVING L 32 - L 37
38-CDB-1 | KT | DB | L38 | 2 | Refuge Area Level 38 | 40-CSMDB-B1 | SERVING L 38 AOR
42-CDB-1 | KT | DB | L42 | 7 | Sky Lobby Level 42 | 40-CSMDB-B1 | SERVING L 39 - L 42
46-CDB-1 | KT | DB | L46 | 3 | Residential Group 1 Level 46 | 40-CSMDB-B1 | SERVING L 43 - L 46
50-CDB-1 | KT | DB | L50 | 2 | Residential Group 1 Level 50 | 40-CSMDB-B1 | SERVING L 47 - L 50
54-CDB-1 | KT | DB | L54 | 2 | Residential Group 1 Level 54 | 40-CSMDB-B1 | SERVING L 51 - L 55
56-CDB-1 | KT | DB | L56 | 3 | Refuge Area Level 56 | 40-CSMDB-B1 | SERVING L 56 AOR
29-ELDB-1 | KT | DB | L29 | 2 | Service Apartments Level 29 | 40-ELSMDB-B2 | SERVING L 27 - L 32
35-ELDB-1 | KT | DB | L35 | 2 | Service Apartments Level 35 | 40-ELSMDB-B2 | SERVING L 33 - L 37
38-ELDB-1 | KT | DB | L38 | 3 | Refuge Area Level 38 | 40-ELSMDB-B2 | SERVING L 38 AOR
40-ELDB-1 | KT | DB | L40 | 11 | MEP Level 40 | 40-ELSMDB-B2 | SERVING L 39 - L 43
46-ELDB-1 | KT | DB | L46 | 4 | Residential Group 1 Level 46 | 40-ELSMDB-B2 | SERVING L 44 - L 49
54-ELDB-1 | KT | DB | L54 | 3 | Residential Group 1 Level 54 | 40-ELSMDB-B2 | SERVING L 50 - L 55
56-ELDB-1 | KT | DB | L56 | 4 | Refuge Area Level 56 | 40-ELSMDB-B2 | SERVING L 56 AOR
71-EVDB-1 | KT | DB | L71 | 2 | Refuge Area Level 71 | 71-EVSMDB-1 | LIFTS
69-EVDB-2 | KT | DB | L69 | 6 | MEP Level 69 | 69-EVSMDB-2 | LIFTS
69-EMDB-A1 | KT | DB | L69 | 7 | MEP Level 69 | 69-ESMDB-B1 | TBC
69-EMDB-B1 | KT | DB | L69 | 8 | MEP Level 69 | 69-ESMDB-B1 | TBC
71-EMDB-1 | KT | DB | L71 | 3 | Refuge Area Level 71 | 69-ESMDB-B1 | SERVING AOR
68-EMDB-A1 | KT | DB | L68 | 7 | MEP Level 68 | 68-ESMDB-B1 | TBC
68-EMDB-B1 | KT | DB | L68 | 8 | MEP Level 68 | 68-ESMDB-B1 | TBC
68-EMDB-B2 | KT | DB | L68 | 9 | MEP Level 68 | 68-ESMDB-B1 | TBC
68-EMDB-C1 | KT | DB | L68 | 10 | MEP Level 68 | 68-ESMDB-B1 | TBC
58-CDB-1 | KT | DB | L58 | 3 | Residential Group 1 Level 58 | 69-CSMDB-B1 | SERVING L 58 - L 61
62-CDB-1 | KT | DB | L62 | 2 | Residential Group 1 Level 62 | 69-CSMDB-B1 | SERVING L 62 - L 65
66-CDB-1 | KT | DB | L66 | 2 | Residential Group 1 Level 66 | 69-CSMDB-B1 | SERVING L 66 - L 69
71-CDB-1 | KT | DB | L71 | 4 | Refuge Area Level 71 | 69-CSMDB-B1 | SERVING L 71 AOR
75-CDB-1 | KT | DB | L75 | 2 | Residential Group 2 Level 75 | 69-CSMDB-B1 | SERVING L 73 - L 76
78-CDB-1 | KT | DB | L78 | 2 | Residential Group 2 Level 78 | 69-CSMDB-B1 | SERVING L 77 - L 80
82-CDB-1 | KT | DB | L82 | 2 | Residential Group 2 Level 82 | 69-CSMDB-B1 | SERVING L 81 - L 84
60-ELDB-1 | KT | DB | L60 | 2 | Residential Group 1 Level 60 | 69-ELSMDB-B2 | SERVING L 58 - L 62
65-ELDB-1 | KT | DB | L65 | 2 | Residential Group 1 Level 65 | 69-ELSMDB-B2 | SERVING L 63 - L 69
71-ELDB-1 | KT | DB | L71 | 5 | Refuge Area Level 71 | 69-ELSMDB-B2 | SERVING L 71 AOR
76-ELDB-1 | KT | DB | L76 | 2 | Residential Group 2 Level 76 | 69-ELSMDB-B2 | SERVING L 73 - L 78
81-ELDB-1 | KT | DB | L81 | 2 | Residential Group 2 Level 81 | 69-ELSMDB-B2 | SERVING L 79 - L 84
B3-EMDB-C1-1 | KT | DB | B3 | 18 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C1-2 | KT | DB | B3 | 19 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C1-3 | KT | DB | B3 | 20 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C2-1 | KT | DB | B3 | 21 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C2-2 | KT | DB | B3 | 22 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C2-3 | KT | DB | B3 | 23 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B3-EMDB-C2-4 | KT | DB | B3 | 24 | Parking/MEP Level B3 | B3-ESMDB-C2-1 | TBC
B2-EMDB-T1-1 | KT | DB | B2 | 46 | Parking/MEP Level B2 | B2-ESMDB-T1-1 | TBC
B2-EMDB-C1-1 | KT | DB | B2 | 47 | Parking/MEP Level B2 | B2-ESMDB-T1-1 | TBC
B1-EMDB-C1-1 | KT | DB | B1 | 16 | Parking Level B1 | B2-ESMDB-T1-1 | TBC
B1-EMDB-C2-1 | KT | DB | B1 | 17 | Parking Level B1 | B2-ESMDB-T1-1 | TBC
B1M-EMDB-T1-1 | KT | DB | B1M | 13 | B1 Mezzanine | B2-ESMDB-T1-1 | TBC
4-EMDB-T1-1 | KT | DB | L4 |  | Spa Level 4 | 4-ESMDB-T1-1 | TBC
5-EMDB-T1-1 | KT | DB | L4 |  | Spa Level 4 | 4-ESMDB-T1-1 | TBC
2-EMDB-T1-1 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
2-EMDB-T1-2 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
2-EMDB-T1-3 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
2M-EMDB-T1-1 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
2M-EMDB-T1-2 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
2M-EMDB-T1-3 | KT | DB | L2 |  | Lobby/Amenities Level 2 | 2-ESMDB-T1-1 | TBC
9-ELDB-1 | KT | DB | L9 | 2 | Office Level 9 | 15-ELSMDB-B1 | SERVING L 7 - L 11
13-ELDB-1 | KT | DB | L13 | 2 | Office Level 13 | 15-ELSMDB-B1 | SERVING L 12 - L 16
18-ELDB-1 | KT | DB | L18 | 2 | Refuge Area Level 18 | 15-ELSMDB-B1 | SERVING L 18 AOR
23-ELDB-1 | KT | DB | L23 | 2 | Hotel Level 23 | 15-ELSMDB-B1 | SERVING L 20 - L 26
7-CDB-1 | KT | DB | L7 | 2 | Office Level 7 | 15-CSMDB-B1 | SERVING L 7 - L 8
9-CDB-1 | KT | DB | L9 | 3 | Office Level 9 | 15-CSMDB-B1 | SERVING L 9 - L 10
12-CDB-1 | KT | DB | L12 | 2 | Office Level 12 | 15-CSMDB-B1 | SERVING L 11 - L 12
13-CDB-1 | KT | DB | L13 | 3 | Office Level 13 | 15-CSMDB-B1 | SERVING L 13
15-CDB-1 | KT | DB | L15 | 6 | MEP Level 15 | 15-CSMDB-B1 | SERVING L 15
16-CDB-1 | KT | DB | L16 | 7 | MEP Level 16 | 15-CSMDB-B1 | SERVING L 16
18-CDB-1 | KT | DB | L18 | 3 | Refuge Area Level 18 | 15-CSMDB-B1 | SERVING L 18 AOR
22-CDB-1 | KT | DB | L22 | 2 | Hotel Level 22 | 15-CSMDB-B1 | SERVING L 20 - L 22
26-CDB-1 | KT | DB | L26 | 2 | Hotel Level 26 | 15-CSMDB-B1 | SERVING L 23 - L 26
15-EMDB-B1 | KT | DB | L15 | 7 | MEP Level 15 | 15-ESMDB-B1 | TBC
15-EMDB-C1 | KT | DB | L15 | 8 | MEP Level 15 | 15-ESMDB-C1 | TBC
16-EMDB-A1 | KT | DB | L16 | 8 | MEP Level 16 | 16-ESMDB-B1 | TBC
16-EMDB-B1 | KT | DB | L16 | 9 | MEP Level 16 | 16-ESMDB-B1 | TBC
16-EMDB-C1 | KT | DB | L16 | 10 | MEP Level 16 | 16-ESMDB-B1 | TBC
18-EMDB-1 | KT | DB | L18 | 4 | MEP Level 18 | 18-ESMDB-1 | TBC
15-EVDB-1 | KT | DB | L15 | 9 | MEP Level 15 | 16-EVSMDB-1 | TBC
16-EVDB-2 | KT | DB | L16 | 11 | MEP Level 16 | 16-EVSMDB-2 | LIFTS
39-EMDB-C1 | KT | DB | L39 | 10 | MEP Level 39 | 39-ESMDB-C1 | TBC
39-EMDB-A1 | KT | DB | L39 | 11 | MEP Level 39 | 39-ESMDB-B2 | TBC
39-EMDB-A2 | KT | DB | L39 | 12 | MEP Level 39 | 39-ESMDB-B2 | TBC
39-EMDB-B1 | KT | DB | L39 | 13 | MEP Level 39 | 39-ESMDB-B2 | TBC
38-EMDB-1 | KT | DB | L38 | 4 | Refuge Area Level 38 | 39-ESMDB-B2 | TBC
4-ELDB-T1 | KT | DB | L4 | 5 | Spa Level 4 | B2-ESMDB-T1-2 | TBC
2-ELDB-T1 | KT | DB | L2 | 6 | Lobby/Amenities Level 2 | B2-ESMDB-T1-2 | TBC
1-ELDB-T1 | KT | DB | L1 | 6 | Lobby/Amenities Level 1 | B2-ESMDB-T1-2 | TBC
B1M-ELDB-T1 | KT | DB | B1M | 14 | B1 Mezzanine | B2-ESMDB-T1-2 | TBC
B1-ELDB-T1 | KT | DB | B1 | 18 | Parking Level B1 | B2-ESMDB-T1-2 | TBC
B2-ELDB-T1 | KT | DB | B2 | 48 | Parking/MEP Level B2 | B2-ESMDB-T1-2 | TBC
B2-ELDB-C1 | KT | DB | B2 | 49 | Parking/MEP Level B2 | B2-ESMDB-T1-2 | TBC
B2-ELDB-T2 | KT | DB | B2 | 50 | Parking/MEP Level B2 | B2-ESMDB-T1-2 | SERVING LOADING DOCK
B3-ELDB-C2 | KT | DB | B3 | 25 | Parking/MEP Level B3 | B2-ESMDB-T1-2 | TBC
B3-CDB-C1-1 | KT | DB | B3 | 26 | Parking/MEP Level B3 | B2-CSMDB-T1-1 | TBC
B2-CDB-T1-1 | KT | DB | B2 | 51 | Parking/MEP Level B2 | B2-CSMDB-T1-1 | TBC
B2-CDB-C1-1 | KT | DB | B2 | 52 | Parking/MEP Level B2 | B2-CSMDB-T1-1 | TBC
B1-CDB-C1-1 | KT | DB | B1 | 19 | Parking Level B1 | B2-CSMDB-T1-1 | TBC
B1-CDB-T1-1 | KT | DB | B1 | 20 | Parking Level B1 | B2-CSMDB-T1-1 | TBC
B1M-CDB-T1-1 | KT | DB | B1M | 15 | B1 Mezzanine | B2-CSMDB-T1-1 | TBC
2-CDB-T1-1 | KT | DB | L2 | 7 | Lobby/Amenities Level 2 | B2-CSMDB-T1-1 | TBC
4-CDB-T1-1 | KT | DB | L4 | 6 | Spa Level 4 | B2-CSMDB-T1-1 | TBC
2M-EVDB-T1-1 | KT | DB | L2 | 8 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-1 | LIFTS
2M-EVDB-T1-2 | KT | DB | L2 | 9 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-2 | LIFTS
2M-EVDB-T1-3 | KT | DB | L2 | 10 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-3 | LIFTS
2M-EVDB-T1-4 | KT | DB | L2 | 11 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-4 | LIFTS
2M-EVDB-T1-5 | KT | DB | L2 | 12 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | LIFTS
2-EVDB-T1-1 | KT | DB | L2 | 13 | Lobby/Amenities Level 2 | 2-EVSMDB-T1-1 | LIFTS
B1-EMDB-B1-1 | KT | DB | B1 | 21 | Parking Level B1 | B1-ESMDB-B1-1 | TBC
B1-EMDB-B1-2 | KT | DB | B1 | 22 | Parking Level B1 | B1-ESMDB-B1-1 | TBC
B1-EMDB-B1-3 | KT | DB | B1 | 23 | Parking Level B1 | B1-ESMDB-B1-1 | TBC
B1-EMDB-B2-1 | KT | DB | B1 | 24 | Parking Level B1 | B1-ESMDB-B1-1 | TBC
B1-EMDB-B2-2 | KT | DB | B1 | 25 | Parking Level B1 | B1-ESMDB-B1-1 | TBC
B3-EMDB-N1 | KT | DB | B3 | 27 | Parking/MEP Level B3 | B3-ESMDB-N-1 | TBC
B3-EMDB-N2 | KT | DB | B3 | 28 | Parking/MEP Level B3 | B3-ESMDB-N-1 | TBC
B3-EMDB-N3 | KT | DB | B3 | 29 | Parking/MEP Level B3 | B3-ESMDB-N-1 | TBC
B3-EMDB-A1-1 | KT | DB | B3 | 30 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A1-2 | KT | DB | B3 | 31 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A1-3 | KT | DB | B3 | 32 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A2-1 | KT | DB | B3 | 33 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A2-2 | KT | DB | B3 | 34 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A2-3 | KT | DB | B3 | 35 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B3-EMDB-A2-4 | KT | DB | B3 | 36 | Parking/MEP Level B3 | B3-ESMDB-A1-1 | TBC
B2-EMDB-A2-1 | KT | DB | B2 | 53 | Parking/MEP Level B2 | B1-ATS-N-1 | TBC
B2-EMDB-A2-2 | KT | DB | B2 | 54 | Parking/MEP Level B2 | B1-ATS-N-1 | TBC
B2-EMDB-A2-3 | KT | DB | B2 | 55 | Parking/MEP Level B2 | B1-ATS-N-1 | TBC
B1-EMDB-A1-1 | KT | DB | B1 | 26 | Parking Level B1 | B1-ESMDB-A1-4 | TBC
B1-EMDB-A1-2 | KT | DB | B1 | 27 | Parking Level B1 | B1-ESMDB-A1-4 | TBC
B1-EMDB-A1-3 | KT | DB | B1 | 28 | Parking Level B1 | B1-ESMDB-A1-4 | TBC
B1-EMDB-A2-1 | KT | DB | B1 | 29 | Parking Level B1 | B1-ESMDB-A2-5 | TBC
B1-EMDB-A2-2 | KT | DB | B1 | 30 | Parking Level B1 | B1-ESMDB-A2-5 | TBC
B1-EMDB-A2-3 | KT | DB | B1 | 31 | Parking Level B1 | B1-ESMDB-A2-5 | TBC
B3-CDB-A2-1 | KT | DB | B3 | 37 | Parking/MEP Level B3 | B1-CSMDB-N-1 | TBC
B2-CDB-A2-1 | KT | DB | B2 | 56 | Parking/MEP Level B2 | B1-CSMDB-N-1 | TBC
B1-CDB-A2-1 | KT | DB | B1 | 32 | Parking Level B1 | B1-CSMDB-N-1 | TBC
B1M-CDB-A2-1 | KT | DB | B1M | 16 | B1 Mezzanine | B1-CSMDB-N-1 | TBC
1-CDB-NG-1 | KT | DB | L1 | 7 | Lobby/Amenities Level 1 | B1-CSMDB-N-1 | TBC
1-CDB-NG-2 | KT | DB | L1 | 8 | Lobby/Amenities Level 1 | 1-CDB-NG-1 | SERVING NORTH GATEHOUSE
B1-ELDB-N | KT | DB | B1 | 33 | Parking Level B1 | B1-ELSMDB-N-2 | TBC
B2-ELDB-A2 | KT | DB | B2 | 57 | Parking/MEP Level B2 | B1-ELSMDB-N-2 | TBC
B3-ELDB-A1 | KT | DB | B3 | 38 | Parking/MEP Level B3 | B1-ELSMDB-N-2 | TBC
B3-EMDB-B1-1 | KT | DB | B3 | 39 | Parking/MEP Level B3 | B3-ESMDB-B1-1 | TBC
B3-EMDB-B1-2 | KT | DB | B3 | 40 | Parking/MEP Level B3 | B3-ESMDB-B1-1 | TBC
B3-EMDB-B1-3 | KT | DB | B3 | 41 | Parking/MEP Level B3 | B3-ESMDB-B1-1 | TBC
B3-EMDB-B1-4 | KT | DB | B3 | 42 | Parking/MEP Level B3 | B3-ESMDB-B1-1 | TBC
B3-EMDB-B1-5 | KT | DB | B3 | 43 | Parking/MEP Level B3 | B3-ESMDB-B1-1 | TBC
B3-EMDB-B2-1 | KT | DB | B3 | 44 | Parking/MEP Level B3 | B3-ESMDB-B2-1 | TBC
B3-EMDB-B2-2 | KT | DB | B3 | 45 | Parking/MEP Level B3 | B3-ESMDB-B2-1 | TBC
B3-EMDB-B2-3 | KT | DB | B3 | 46 | Parking/MEP Level B3 | B3-ESMDB-B2-1 | TBC
B3-EMDB-B2-4 | KT | DB | B3 | 47 | Parking/MEP Level B3 | B3-ESMDB-B2-1 | TBC
B2-EMDB-B1-1 | KT | DB | B2 | 58 | Parking/MEP Level B2 | B2-ESMDB-B2-2 | TBC
B2-EMDB-B1-2 | KT | DB | B2 | 59 | Parking/MEP Level B2 | B2-ESMDB-B2-2 | TBC
B2-EMDB-B1-3 | KT | DB | B2 | 60 | Parking/MEP Level B2 | B2-ESMDB-B2-2 | TBC
B2-EMDB-B2-1 | KT | DB | B2 | 61 | Parking/MEP Level B2 | B2-ESMDB-B2-2 | TBC
B2-EMDB-B2-2 | KT | DB | B2 | 62 | Parking/MEP Level B2 | B2-ESMDB-B2-2 | TBC
B3-CDB-B1 | KT | DB | B3 | 48 | Parking/MEP Level B3 | B2-CSMDB-S-1 | TBC
B2-CDB-B1 | KT | DB | B2 | 63 | Parking/MEP Level B2 | B2-CSMDB-S-1 | TBC
B2-CDB-SG-1 | KT | DB | B2 | 64 | Parking/MEP Level B2 | B2-CSMDB-S-1 | TBC
B1M-CDB-B1 | KT | DB | B1M | 17 | B1 Mezzanine | B2-CSMDB-S-1 | TBC
1-CDB-SG-1 | KT | DB | L1 | 9 | Lobby/Amenities Level 1 | B2-CSMDB-S-1 | TBC
1-CDB-SG-2 | KT | DB | L1 | 10 | Lobby/Amenities Level 1 | 1-CDB-SG-1 | SERVING SOUTH GATEHOUSE
B2-ELDB-B1 | KT | DB | B2 | 65 | Parking/MEP Level B2 | B2-ELSMDB-S-2 | SERVING LEVELS B 3 - B 1
B2-ELDB-B2 | KT | DB | B2 | 66 | Parking/MEP Level B2 | B2-ELSMDB-S-2 | SERVING LEVELS B 3 - B 1
B2-ELDB-S | KT | DB | B2 | 67 | Parking/MEP Level B2 | B2-ELSMDB-S-2 | SERVING LEVELS B 3 - B 1
UPS 80KVA | KT | UPS | L96 | 1 | MEP Level 96 | 96-CSMDB-1 | NETPOP "C"
UPS 80KVA | KT | UPS | L15 | 1 | MEP Level 15 | 15-CSMDB-B1 | NETPOP "B"
UPS 120KVA | KT | UPS | B1 | 1 | Parking Level B1 | B2-CSMDB-T1-1 | SECURITY SUITE
UPS DB | KT | UPS | B2 | 1 | Parking/MEP Level B2 | UPS 120KVA | "A"
UPS DB | KT | UPS | B2 | 2 | Parking/MEP Level B2 | UPS 120KVA | "B"
UPS 200KVA | KT | UPS | B2 | 3 | Parking/MEP Level B2 | B2-CSMDB-T1-1 | NETPOP "A"
UPS DB | KT | UPS | B2 | 4 | Parking/MEP Level B2 | UPS 200KVA | "A"
UPS DB | KT | UPS | B2 | 5 | Parking/MEP Level B2 | UPS 200KVA | "B"
UPS DB | KT | UPS | B2 | 6 | Parking/MEP Level B2 | UPS 200KVA | "A"
UPS DB | KT | UPS | B2 | 7 | Parking/MEP Level B2 | UPS 200KVA | "B"
UPS 80KVA | KT | UPS | B1 | 2 | Parking Level B1 | B1-CSMDB-N-1 | TELCOM ENTRANCE FACILITY "B"
UPS 30KVA | KT | UPS | B1 | 3 | Parking Level B1 | B1-CSMDB-N-1 | SERVING NORTH GATEHOUSE FACILITY
UPS 100KVA | KT | UPS | B1 | 4 | Parking Level B1 | B1-CSMDB-N-1 | L2 BOC
UPS 80KVA | KT | UPS | B2 | 8 | Parking/MEP Level B2 | B2-CSMDB-S-1 | TELECOM ENTRANCE FACILITY "A"
UPS 30KVA | KT | UPS | B2 | 9 | Parking/MEP Level B2 | B2-CSMDB-S-1 | SERVING SOUTH GATEHOUSE FACILITY
630A CB | KT | CB | L10 | 1 | Office Level 10 | 2000A PLUG-IN BUSWAY | 13-BSMDB-1
630A CB | KT | CB | L9 | 1 | Office Level 9 | 2000A PLUG-IN BUSWAY | 12-BSMDB-1
630A CB | KT | CB | L8 | 1 | Office Level 8 | 2000A PLUG-IN BUSWAY | 11-BSMDB-1
630A CB | KT | CB | L7 | 1 | Office Level 7 | 2000A PLUG-IN BUSWAY | 10-BSMDB-1
630A CB | KT | CB | L13 | 1 | Office Level 13 | 1600A PLUG-IN BUSWAY | 9-BSMDB-1
630A CB | KT | CB | L12 | 1 | Office Level 12 | 1600A PLUG-IN BUSWAY | 8-BSMDB-1
630A CB | KT | CB | L11 | 1 | Office Level 11 | 1600A PLUG-IN BUSWAY | 7-BSMDB-1
300A CB | KT | CB | L18 | 1 | Refuge Area Level 18 | 1600A PLUG-IN BUSWAY | 18-PDB-1
300A CB | KT | CB | L20 | 1 | Hotel Level 20 | 1600A PLUG-IN BUSWAY | 20-BSMDB-1
300A CB | KT | CB | L21 | 1 | Hotel Level 21 | 1600A PLUG-IN BUSWAY | 21-BSMDB-1
300A CB | KT | CB | L22 | 1 | Hotel Level 22 | 1600A PLUG-IN BUSWAY | 22-BSMDB-1
300A CB | KT | CB | L23 | 1 | Hotel Level 23 | 1600A PLUG-IN BUSWAY | 23-BSMDB-1
300A CB | KT | CB | L24 | 1 | Hotel Level 24 | 1600A PLUG-IN BUSWAY | 24-BSMDB-1
300A CB | KT | CB | L25 | 1 | Hotel Level 25 | 1600A PLUG-IN BUSWAY | 25-BSMDB-1
300A CB | KT | CB | L26 | 1 | Hotel Level 26 | 1600A PLUG-IN BUSWAY | 26-BSMDB-1
150A CB | KT | CB | L27 | 1 | Service Apartments Level 27 | 2000A PLUG-IN BUSWAY | 27-BSMDB-1
150A CB | KT | CB | L28 | 1 | Service Apartments Level 28 | 2000A PLUG-IN BUSWAY | 28-BSMDB-1
150A CB | KT | CB | L29 | 1 | Service Apartments Level 29 | 2000A PLUG-IN BUSWAY | 29-BSMDB-1
150A CB | KT | CB | L30 | 1 | Service Apartments Level 30 | 2000A PLUG-IN BUSWAY | 30-BSMDB-1
150A CB | KT | CB | L31 | 1 | Service Apartments Level 31 | 2000A PLUG-IN BUSWAY | 31-BSMDB-1
150A CB | KT | CB | L32 | 1 | Service Apartments Level 32 | 2000A PLUG-IN BUSWAY | 32-BSMDB-1
150A CB | KT | CB | L33 | 1 | Service Apartments Level 33 | 2000A PLUG-IN BUSWAY | 33-BSMDB-1
150A CB | KT | CB | L34 | 1 | Service Apartments Level 34 | 2000A PLUG-IN BUSWAY | 34-BSMDB-1
150A CB | KT | CB | L35 | 1 | Service Apartments Level 35 | 2000A PLUG-IN BUSWAY | 35-BSMDB-1
150A CB | KT | CB | L36 | 1 | Service Apartments Level 36 | 2000A PLUG-IN BUSWAY | 36-BSMDB-1
150A CB | KT | CB | L37 | 1 | Service Apartments Level 37 | 2000A PLUG-IN BUSWAY | 37-BSMDB-1
150A CB | KT | CB | L38 | 1 | Service Apartments Level 38 | 2000A PLUG-IN BUSWAY | 38-BSMDB-1
100A CB | KT | CB | B1 | 1 | B1 Mezzanine | B1M-MSMDB-T1-1 | WH-1 LEVEL B1M
100A CB | KT | CB | L1 | 1 | Lobby/Amenities Level 1 | 1-MSMDB-T1-1 | WH-1 LEVEL 1
100A CB | KT | CB | L1 | 2 | Lobby/Amenities Level 1 | 1-MSMDB-T1-1 | WH-1 LEVEL 1
100A CB | KT | CB | L1 | 3 | Lobby/Amenities Level 1 | 1-MSMDB-T1-1 | WH-1 LEVEL 1
100A CB | KT | CB | L1 | 4 | Lobby/Amenities Level 1 | 1-MSMDB-T1-1 | WH-1 LEVEL 1
200A CB | KT | CB | L1 | 5 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | ES01
200A CB | KT | CB | L1 | 6 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | ES02
200A CB | KT | CB | L1 | 7 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | ES05
200A CB | KT | CB | L1 | 8 | Lobby/Amenities Level 1 | 1-BSMDB-T1-1 | ES06
200A CB | KT | CB | B2 | 1 | Parking/MEP Level B2 | B1-MSMDB-A1-1 | ES07
200A CB | KT | CB | B2 | 2 | Parking/MEP Level B2 | B1-MSMDB-A1-1 | ES08
200A CB | KT | CB | B2 | 3 | Parking/MEP Level B2 | B1-MSMDB-A1-1 | ES03
200A CB | KT | CB | B2 | 4 | Parking/MEP Level B2 | B1-MSMDB-A1-1 | ES04
100 CB | KT | CB | B2 | 5 | Parking/MEP Level B2 | B2-MSMDB-A1-1 | WH-1 LEVEL B2
200A CB | KT | CB | L99 | 1 | Residential Group 4 Level 99 | 1600A PLUG-IN BUSWAY | 99-BSMDB-1
200A CB | KT | CB | L100 | 1 | Residential Group 4 Level 100 | 1600A PLUG-IN BUSWAY | 100-BSMDB-1
200A CB | KT | CB | L101 | 1 | Residential Group 4 Level 101 | 1600A PLUG-IN BUSWAY | 101-BSMDB-1
200A CB | KT | CB | L102 | 1 | Residential Group 4 Level 102 | 1600A PLUG-IN BUSWAY | 102-BSMDB-1
200A CB | KT | CB | L103 | 1 | Residential Group 4 Level 103 | 1600A PLUG-IN BUSWAY | 103-BSMDB-1
200A CB | KT | CB | L104 | 1 | Refuge Area Level 104 | 1600A PLUG-IN BUSWAY | 104-PDB-1
300A CB | KT | CB | L94 | 1 | Residential Group 3 Level 94 | 1600A PLUG-IN BUSWAY | 94-BSMDB-1
300A CB | KT | CB | L93 | 1 | Residential Group 3 Level 93 | 1600A PLUG-IN BUSWAY | 93-BSMDB-1
300A CB | KT | CB | L92 | 1 | Residential Group 3 Level 92 | 1600A PLUG-IN BUSWAY | 92-BSMDB-1
300A CB | KT | CB | L91 | 1 | Residential Group 3 Level 91 | 1600A PLUG-IN BUSWAY | 91-BSMDB-1
300A CB | KT | CB | L90 | 1 | Residential Group 3 Level 90 | 1600A PLUG-IN BUSWAY | 90-BSMDB-1
300A CB | KT | CB | L89 | 1 | Residential Group 3 Level 89 | 1600A PLUG-IN BUSWAY | 89-BSMDB-1
300A CB | KT | CB | L88 | 1 | Residential Group 3 Level 88 | 1600A PLUG-IN BUSWAY | 88-BSMDB-1
300A CB | KT | CB | L87 | 1 | Residential Group 3 Level 87 | 1600A PLUG-IN BUSWAY | 87-BSMDB-1
300A CB | KT | CB | L86 | 1 | Refuge Area Level 86 | 1600A PLUG-IN BUSWAY | 86-PDB-1
400A CB | KT | CB | L95 | 1 | MEP Level 95 | 95-MSMDB-C1 | WH-5
400A CB | KT | CB | L95 | 2 | MEP Level 95 | 95-MSMDB-C1 | WH-5
400A CB | KT | CB | L95 | 3 | MEP Level 95 | 95-MSMDB-C1 | WH-5
200A CB | KT | CB | L120 | 1 | Residential Group 4 Level 120 | 2500A PLUG-IN BUSWAY | 120-BSMDB-1
200A CB | KT | CB | L119 | 1 | Residential Group 4 Level 119 | 2500A PLUG-IN BUSWAY | 119-BSMDB-1
200A CB | KT | CB | L118 | 1 | Residential Group 4 Level 118 | 2500A PLUG-IN BUSWAY | 118-BSMDB-1
200A CB | KT | CB | L117 | 1 | Residential Group 4 Level 117 | 2500A PLUG-IN BUSWAY | 117-BSMDB-1
200A CB | KT | CB | L116 | 1 | Residential Group 4 Level 116 | 2500A PLUG-IN BUSWAY | 116-BSMDB-1
200A CB | KT | CB | L115 | 1 | Residential Group 4 Level 115 | 2500A PLUG-IN BUSWAY | 115-BSMDB-1
200A CB | KT | CB | L114 | 1 | Residential Group 4 Level 114 | 2500A PLUG-IN BUSWAY | 114-BSMDB-1
200A CB | KT | CB | L113 | 1 | Residential Group 4 Level 113 | 2500A PLUG-IN BUSWAY | 113-BSMDB-1
200A CB | KT | CB | L112 | 1 | Residential Group 4 Level 112 | 2500A PLUG-IN BUSWAY | 112-BSMDB-1
200A CB | KT | CB | L111 | 1 | Residential Group 4 Level 111 | 2500A PLUG-IN BUSWAY | 111-BSMDB-1
200A CB | KT | CB | L110 | 1 | Residential Group 4 Level 110 | 2500A PLUG-IN BUSWAY | 110-BSMDB-1
200A CB | KT | CB | L109 | 1 | Residential Group 4 Level 109 | 2500A PLUG-IN BUSWAY | 109-BSMDB-1
200A CB | KT | CB | L108 | 1 | Residential Group 4 Level 108 | 2500A PLUG-IN BUSWAY | 108-BSMDB-1
200A CB | KT | CB | L107 | 1 | Residential Group 4 Level 107 | 2500A PLUG-IN BUSWAY | 107-BSMDB-1
200A CB | KT | CB | L106 | 1 | Residential Group 4 Level 106 | 2500A PLUG-IN BUSWAY | 106-BSMDB-1
300A CB | KT | CB | L121 | 1 | MEP Level 121 | 121-MSMDB-C | WH-6
300A CB | KT | CB | L121 | 2 | MEP Level 121 | 121-MSMDB-C | WH-6
300A CB | KT | CB | L121 | 3 | MEP Level 121 | 121-MSMDB-1 | WH-6
400A CB | KT | CB | L67 | 1 | Residential Group 4 Level 67 | 2500A PLUG-IN BUSWAY | 67-BSMDB-1
400A CB | KT | CB | L66 | 1 | Residential Group 4 Level 66 | 2500A PLUG-IN BUSWAY | 66-BSMDB-1
400A CB | KT | CB | L65 | 1 | Residential Group 4 Level 65 | 2500A PLUG-IN BUSWAY | 65-BSMDB-1
400A CB | KT | CB | L64 | 1 | Residential Group 4 Level 64 | 2500A PLUG-IN BUSWAY | 64-BSMDB-1
400A CB | KT | CB | L63 | 1 | Residential Group 4 Level 63 | 2500A PLUG-IN BUSWAY | 63-BSMDB-1
400A CB | KT | CB | L62 | 1 | Residential Group 4 Level 62 | 2500A PLUG-IN BUSWAY | 62-BSMDB-1
400A CB | KT | CB | L61 | 1 | Residential Group 4 Level 61 | 2500A PLUG-IN BUSWAY | 61-BSMDB-1
400A CB | KT | CB | L60 | 1 | Residential Group 4 Level 60 | 2500A PLUG-IN BUSWAY | 60-BSMDB-1
400A CB | KT | CB | L59 | 1 | Residential Group 4 Level 59 | 2500A PLUG-IN BUSWAY | 59-BSMDB-1
400A CB | KT | CB | L58 | 1 | Residential Group 4 Level 58 | 2500A PLUG-IN BUSWAY | 58-BSMDB-1
100A CB | KT | CB | L68 | 1 | MEP Level 68 | 68-MSMDB-C1 | CHWP-68-5
630A CB | KT | CB | L68 | 2 | MEP Level 68 | 68-MSMDB-C1 | WH-4
630A CB | KT | CB | L68 | 3 | MEP Level 68 | 68-MSMDB-B2 | WH-4
630A CB | KT | CB | L68 | 4 | MEP Level 68 | 68-MSMDB-B2 | WH-4
200 CB | KT | CB | L71 | 1 | Refuge Area Level 71 | 2500A PLUG-IN BUSWAY | 71-PDB-1
250A CB | KT | CB | L73 | 1 | Resudential Group 2 Level 73 | 2500A PLUG-IN BUSWAY | 73-BSMDB-1
300A CB | KT | CB | L74 | 1 | Resudential Group 2 Level 74 | 2500A PLUG-IN BUSWAY | 74-BSMDB-1
250A CB | KT | CB | L75 | 1 | Resudential Group 2 Level 75 | 2500A PLUG-IN BUSWAY | 75-BSMDB-1
300A CB | KT | CB | L76 | 1 | Resudential Group 2 Level 76 | 2500A PLUG-IN BUSWAY | 76-BSMDB-1
250A CB | KT | CB | L77 | 1 | Resudential Group 2 Level 77 | 2500A PLUG-IN BUSWAY | 77-BSMDB-1
300A CB | KT | CB | L78 | 1 | Resudential Group 2 Level 78 | 2500A PLUG-IN BUSWAY | 78-BSMDB-1
250A CB | KT | CB | L79 | 1 | Resudential Group 2 Level 79 | 2500A PLUG-IN BUSWAY | 79-BSMDB-1
250A CB | KT | CB | L80 | 1 | Resudential Group 2 Level 80 | 2500A PLUG-IN BUSWAY | 80-BSMDB-1
300A CB | KT | CB | L81 | 1 | Resudential Group 2 Level 81 | 2500A PLUG-IN BUSWAY | 81-BSMDB-1
250A CB | KT | CB | L82 | 1 | Resudential Group 2 Level 82 | 2500A PLUG-IN BUSWAY | 82-BSMDB-1
300A CB | KT | CB | L83 | 1 | Resudential Group 2 Level 83 | 2500A PLUG-IN BUSWAY | 83-BSMDB-1
300A CB | KT | CB | L84 | 1 | Sky Lobby Level 84 | 2500A PLUG-IN BUSWAY | 84-BSMDB-1
400A CB | KT | CB | L42 | 1 | Sky Lobby Level 42 | 3000A PLUG-IN BUSWAY | 42-BSMDB-1
400A CB | KT | CB | L43 | 1 | Sky Lobby Level 43 | 3000A PLUG-IN BUSWAY | 43-BSMDB-1
250A CB | KT | CB | L44 | 1 | Residential Group 1 Level 44 | 3000A PLUG-IN BUSWAY | 44-BSMDB-1
250A CB | KT | CB | L45 | 1 | Residential Group 1 Level 45 | 3000A PLUG-IN BUSWAY | 45-BSMDB-1
250A CB | KT | CB | L46 | 1 | Residential Group 1 Level 46 | 3000A PLUG-IN BUSWAY | 46-BSMDB-1
250A CB | KT | CB | L47 | 1 | Residential Group 1 Level 47 | 3000A PLUG-IN BUSWAY | 47-BSMDB-1
250A CB | KT | CB | L48 | 1 | Residential Group 1 Level 48 | 3000A PLUG-IN BUSWAY | 48-BSMDB-1
250A CB | KT | CB | L49 | 1 | Residential Group 1 Level 49 | 3000A PLUG-IN BUSWAY | 49-BSMDB-1
250A CB | KT | CB | L50 | 1 | Residential Group 1 Level 50 | 3000A PLUG-IN BUSWAY | 50-BSMDB-1
250A CB | KT | CB | L51 | 1 | Residential Group 1 Level 51 | 3000A PLUG-IN BUSWAY | 51-BSMDB-1
250A CB | KT | CB | L52 | 1 | Residential Group 1 Level 52 | 3000A PLUG-IN BUSWAY | 52-BSMDB-1
250A CB | KT | CB | L53 | 1 | Residential Group 1 Level 53 | 3000A PLUG-IN BUSWAY | 53-BSMDB-1
250A CB | KT | CB | L54 | 1 | Residential Group 1 Level 54 | 3000A PLUG-IN BUSWAY | 54-BSMDB-1
250A CB | KT | CB | L55 | 1 | Residential Group 1 Level 55 | 3000A PLUG-IN BUSWAY | 55-BSMDB-1
250A CB | KT | CB | L56 | 1 | Refuge Area Level 56 | 3000A PLUG-IN BUSWAY | 56-PDB-1
350A CB | KT | CB | L39 | 1 | MEP Level 39 | 39-MSMDB-C1 | WH-3-1
350A CB | KT | CB | L39 | 2 | MEP Level 39 | 39-MSMDB-C1 | WH-3-2
350A CB | KT | CB | L39 | 3 | MEP Level 39 | 39-MSMDB-B1 | WH-3-3
63A CB | KT | CB | L162 | 1 | MEP Level 162 | 162-ESMDB-1 | 168-BME-1
63A CB | KT | CB | L162 | 2 | MEP Level 162 | 162-ESMDB-1 | 168-BME-2
63A CB | KT | CB | L162 | 3 | MEP Level 162 | 162-ESMDB-1 | 168-BME-3
63A CB | KT | CB | L155 | 1 | BMU/MEP Level 155 | 155-ESMDB-1 | 156-BME-1
63A CB | KT | CB | L155 | 2 | BMU/MEP Level 155 | 155-ESMDB-1 | 156-BME-2
800A CB | KT | CB | L162 | 4 | MEP Level 162 | 162-EVSMDB-1 | ELEVATOR OB1
800A CB | KT | CB | L162 | 5 | MEP Level 162 | 162-EVSMDB-1 | ELEVATOR OB2
125A CB | KT | CB | L162 | 6 | MEP Level 162 | 162-EVSMDB-1 | ELEVATOR OR1
125A CB | KT | CB | L162 | 7 | MEP Level 162 | 162-EVSMDB-1 | ELEVATOR OR2
500A CB | KT | CB | L171 | 1 | TMD Reserve Level 171 | 171-EVSMDB-1 | ELEVATOR S3
630A CB | KT | CB | L171 | 2 | TMD Reserve Level 171 | 171-EVSMDB-1 | ELEVATOR FS2
50A CB | KT | CB | L171 | 3 | TMD Reserve Level 171 | 171-EVSMDB-1 | ELEVATOR WL1
350A CB | KT | CB | L88 | 2 | Residential Group 3A Level 88 | 88/89-EV-SMDB-1 | ELEVATOR RS4
350A CB | KT | CB | L88 | 3 | Residential Group 3A Level 88 | 88/89-EV-SMDB-1 | ELEVATOR RS5
350A CB | KT | CB | L88 | 4 | Residential Group 3A Level 88 | 88/89-EV-SMDB-1 | ELEVATOR RS6
350A CB | KT | CB | L85 | 1 | Sky Lobby Level 85 | 85-EVSMDB-1 | ELEVATOR R4
350A CB | KT | CB | L85 | 2 | Sky Lobby Level 85 | 85-EVSMDB-1 | ELEVATOR R5
350A CB | KT | CB | L85 | 3 | Sky Lobby Level 85 | 85-EVSMDB-1 | ELEVATOR R6
200A CB | KT | CB | L121 | 4 | MEP Level 121 | 121-EVSMDB-1 | ELEVATOR R7
200A CB | KT | CB | L121 | 5 | MEP Level 121 | 121-EVSMDB-1 | ELEVATOR R8
200A CB | KT | CB | L121 | 6 | MEP Level 121 | 121-EVSMDB-1 | ELEVATOR R9
63A CB | KT | CB | L122 | 1 | MEP Level 122 | 122-ESMDB-B2 | BME-1
63A CB | KT | CB | L122 | 2 | MEP Level 122 | 122-ESMDB-B2 | BME-2
63A CB | KT | CB | L122 | 3 | MEP Level 122 | 122-ESMDB-B2 | BME-3
160A CB | KT | CB | L28 | 2 | Service Apartments Level 28 | 28/29-EVSMDB-1 | ELEVATOR H1
160A CB | KT | CB | L28 | 3 | Service Apartments Level 28 | 28/29-EVSMDB-1 | ELEVATOR H2
160A CB | KT | CB | L28 | 4 | Service Apartments Level 28 | 28/29-EVSMDB-1 | ELEVATOR H3
200A CB | KT | CB | L39 | 4 | MEP Level 39 | 39-EVSMDB-1 | ELEVATOR HS1
200A CB | KT | CB | L39 | 5 | MEP Level 39 | 39-EVSMDB-1 | ELEVATOR HS2
200A CB | KT | CB | L39 | 6 | MEP Level 39 | 39-EVSMDB-2 | ELEVATOR A1
200A CB | KT | CB | L39 | 7 | MEP Level 39 | 39-EVSMDB-2 | ELEVATOR A2
200A CB | KT | CB | L39 | 8 | MEP Level 39 | 39-EVSMDB-2 | ELEVATOR A3
500A CB | KT | CB | L46 | 2 | Residential Group 1 Level 46 | 46-EVSMDB-1 | ELEVATOR RS1
500A CB | KT | CB | L46 | 3 | Residential Group 1 Level 46 | 46-EVSMDB-1 | ELEVATOR RS2
500A CB | KT | CB | L46 | 4 | Residential Group 1 Level 46 | 46-EVSMDB-1 | ELEVATOR RS3
630A CB | KT | CB | L71 | 2 | Refuge Area Level 71 | 71-EVSMDB-1 | ELEVATOR FS1
200A CB | KT | CB | L69 | 1 | MEP Level 69 | 69-EVSMDB-2 | ELEVATOR R1
200A CB | KT | CB | L69 | 2 | MEP Level 69 | 69-EVSMDB-2 | ELEVATOR R2
200A CB | KT | CB | L69 | 3 | MEP Level 69 | 69-EVSMDB-2 | ELEVATOR R3
63A CB | KT | CB | L69 | 4 | MEP Level 69 | 69-ESMDB-B1 | BME-69-1
63A CB | KT | CB | L69 | 5 | MEP Level 69 | 69-ESMDB-B1 | BME-69-2
63A CB | KT | CB | L69 | 6 | MEP Level 69 | 69-ESMDB-B1 | BME-69-3
400A CB | KT | CB | L71 | 3 | Refuge Area Level 71 | 71-EVSMDB-3 | ELEVATOR S1
400A CB | KT | CB | L71 | 4 | Refuge Area Level 71 | 71-EVSMDB-3 | ELEVATOR S2
100A CB | KT | CB | L15 | 1 | MEP Level 15 | 15-ESMDB-B1 | AHU-15-13
100A CB | KT | CB | L18 | 2 | MEP Level 18 | 18-ESMDB-1 | AIR COMPRESSOR 22KW
150A CB | KT | CB | L16 | 1 | MEP Level 162 | 16-EVSMDB-1 | ELEVATOR O1
150A CB | KT | CB | L16 | 2 | MEP Level 162 | 16-EVSMDB-1 | ELEVATOR O2
150A CB | KT | CB | L16 | 3 | MEP Level 162 | 16-EVSMDB-1 | ELEVATOR O3
150A CB | KT | CB | L16 | 4 | MEP Level 162 | 16-EVSMDB-1 | ELEVATOR O4
150A CB | KT | CB | L16 | 5 | MEP Level 162 | 16-EVSMDB-1 | ELEVATOR O5
200A CB | KT | CB | L16 | 6 | MEP Level 162 | 16-EVSMDB-2 | ELEVATOR OS1
200A CB | KT | CB | L2 | 1 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-1 | ELEVATOR OP1
200A CB | KT | CB | L2 | 2 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-1 | ELEVATOR OP2
200A CB | KT | CB | L2 | 3 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-1 | ELEVATOR OP3
200A CB | KT | CB | L2 | 4 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-1 | ELEVATOR OP4
200A CB | KT | CB | L2 | 5 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-2 | ELEVATOR AP1
200A CB | KT | CB | L2 | 6 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-2 | ELEVATOR AP2
200A CB | KT | CB | L2 | 7 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-3 | ELEVATOR RP1
200A CB | KT | CB | L2 | 8 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-3 | ELEVATOR RP2
200A CB | KT | CB | L2 | 9 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-3 | ELEVATOR RP3
200A CB | KT | CB | L2 | 10 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-3 | ELEVATOR RP4
200A CB | KT | CB | L2 | 11 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-4 | ELEVATOR HP1
200A CB | KT | CB | L2 | 12 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-4 | ELEVATOR HP2
200A CB | KT | CB | L2 | 13 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | ELEVATOR HS3
200A CB | KT | CB | L2 | 14 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | ELEVATOR HS4
200A CB | KT | CB | L2 | 15 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | ELEVATOR HS5
200A CB | KT | CB | L2 | 16 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | ELEVATOR HS6
200A CB | KT | CB | L2 | 17 | Lobby/Amenities Level 2 | 2M-EVSMDB-T1-5 | ELEVATOR HS7
200A CB | KT | CB | L2 | 18 | Lobby/Amenities Level 2 | 2-EVSMDB-T1-1 | ELEVATOR B1
200A CB | KT | CB | L2 | 19 | Lobby/Amenities Level 2 | 2-EVSMDB-T1-1 | ELEVATOR B2